ORDER No. R2-2017-00XX

NPDES No. CA0038849

**WASTE DISCHARGE REQUIREMENTS FOR MERCURY AND PCBS FROM MUNICIPAL AND INDUSTRIAL WASTEWATER DISCHARGES TO SAN FRANCISCO BAY**

The following dischargers are subject to waste discharge requirements (WDRs) set forth in this Order, for the purpose of implementing the San Francisco Bay Mercury and PCBs Total Maximum Daily Load (TMDL) wasteload allocations for municipal and industrial wastewater discharges to San Francisco Bay and its contiguous bay segments:

Table 1A. Municipal Discharger Information

| **Discharger** | **Facility Name** | **Facility Address** | **Minor/ Major** |
| --- | --- | --- | --- |
| American Canyon, City of | Wastewater Treatment and Reclamation Facility | 151 Mezzetta Court  American Canyon, CA 94503  Napa County | Major |
| Benicia, City of | Benicia Wastewater Treatment Plant | 614 East Fifth Street  Benicia, CA 94510  Solano County | Major |
| Burlingame, City of | Burlingame Wastewater Treatment Plant | 1103 Airport Boulevard  Burlingame, CA 94010  San Mateo County | Major |
| Calistoga, City of | Dunaweal Wastewater Treatment Plant | 1100 Dunaweal Lane  Calistoga, CA 94515  Napa County | Minor |
| Central Contra Costa Sanitary District | Central Contra Costa Sanitary District Wastewater Treatment Plant | 5019 Imhoff Place  Martinez, CA 94553  Contra Costa County | Major |
| Central Marin Sanitation Agency | Central Marin Sanitation Agency Wastewater Treatment Plant | 1301 Andersen Drive  San Rafael, CA 94901  Marin County | Major |
| Crockett Community Services District | Port Costa Wastewater Treatment Plant | End of Canyon Lake Drive  Port Costa, CA 94569  Contra Costa County | Minor |
| Delta Diablo Sanitation District | Delta Diablo Wastewater Treatment Plant | 2500 Pittsburg-Antioch Highway Antioch, CA 94509  Contra Costa County | Major |
| East Bay Dischargers Authority (EBDA); Cities of Hayward and San Leandro; Oro Loma Sanitary District; Castro Valley Sanitary District; Union Sanitary District; Livermore-Amador Valley Water Management Agency; Dublin San Ramon Services District; and City of Livermore | EBDA Common Outfall | EBDA Common Outfall  14150 Monarch Bay Drive  San Leandro, CA 94577  Alameda County | Major |
| Hayward Water Pollution Control Facility |
| San Leandro Water Pollution Control Plant |
| Oro Loma/Castro Valley Sanitary Districts Water Pollution Control Plant |
| Raymond A. Boege Alvarado Wastewater Treatment Plant |
| Livermore-Amador Valley Water Management Agency Export and Storage Facilities |
| Dublin San Ramon Services District Wastewater Treatment Plant |
| City of Livermore Water Reclamation Plant |
| East Bay Municipal Utility District | East Bay Municipal Utility District, Special District No. 1 Wastewater Treatment Plant (WWTP) | 2020 Wake Avenue  Oakland, CA 94607  Alameda County | Major |
| Fairfield-Suisun Sewer District | Fairfield-Suisun Wastewater Treatment Plant | 1010 Chadbourne Road  Fairfield, CA 94534  Solano County | Major |
| Las Gallinas Valley Sanitary District | Las Gallinas Valley Sanitary District Sewage Treatment Plant | 300 Smith Ranch Road  San Rafael, CA 94903  Marin County | Major |
| Marin County (Paradise Cove), Sanitary District No. 5 of | Paradise Cove Treatment Plant | 3700 Paradise Drive  Tiburon, CA 94920  Marin County | Minor |
| Marin County (Tiburon), Sanitary District No. 5 of | Wastewater Treatment Plant | 2001 Paradise Drive  Tiburon, CA 94920  Marin County | Major |
| Millbrae, City of | Water Pollution Control Plant | 400 East Millbrae Avenue  Millbrae, CA 94030  San Mateo County | Major |
| Mt. View Sanitary District | Mt. View Sanitary District Wastewater Treatment Plant | 3800 Arthur Road  Martinez, CA 94553  Contra Costa County | Major |
| Napa Sanitation District | Soscol Water Recycling Facility | 1515 Soscol Ferry Road  Napa, CA 94558  Napa County | Major |
| Novato Sanitary District | Novato Sanitary District Wastewater Treatment Plant | 500 Davidson Street  Novato, CA 94945  Marin County | Major |
| Palo Alto, City of | Palo Alto Regional Water Quality Control Plant | 2501 Embarcadero Way  Palo Alto, CA 94303  Santa Clara County | Major |
| Petaluma, City of | Municipal Wastewater Treatment Plant | 3890 Cypress Drive  Petaluma, CA 94954  Sonoma County | Major |
| Pinole, City of | Pinole-Hercules Water Pollution Control Plant | 11 Tennent Avenue  Pinole, CA, 94564  Contra Costa County | Major |
| Rodeo Sanitary District | Rodeo Sanitary District Water Pollution Control Facility | 800 San Pablo Avenue  Rodeo, CA 94572  Contra Costa County | Major |
| Saint Helena, City of | City of St. Helena Wastewater Treatment and Reclamation Plant | 1 Thomann Lane  St. Helena, CA 94574  Napa County | Minor |
| San Francisco (San Francisco International Airport), City and County of | Mel Leong Treatment Plant, Sanitary Plant | Bldg. 924 Clearwater Drive  San Francisco, CA 94128  San Mateo County | Major |
| San Francisco (Southeast Plant), City and County of | Southeast Water Pollution Control Plant | 750 Phelps Street  San Francisco, CA 94124  San Francisco County | Major |
| San Jose and Santa Clara, Cities of | San Jose/Santa Clara Water Pollution Control Plant | 700 Los Esteros Road  San Jose, CA 95134  Santa Clara County | Major |
| San Mateo, City of | City of San Mateo Wastewater Treatment Plant | 2050 Detroit Drive  San Mateo, CA 94404  San Mateo County | Major |
| Sausalito-Marin City Sanitary District | Sausalito-Marin City Sanitary District Wastewater Treatment Plant | 1 East Road  Sausalito, CA 94965  Marin County | Major |
| Sewerage Agency of Southern Marin | Wastewater Treatment Plant | 450 Sycamore Avenue  Mill Valley, CA 94941  Marin County | Major |
| Silicon Valley Clean Water | Silicon Valley Clean Water Wastewater Treatment Plant | 1400 Radio Road  Redwood City, CA 94065  San Mateo County | Major |
| Sonoma Valley County Sanitation District | Municipal Wastewater Treatment Plant | 22675 8th Street East  Sonoma, CA 95476  Sonoma County | Major |
| South San Francisco and San Bruno, Cities of | South San Francisco and San Bruno Water Quality Control Plant | 195 Belle Air Road  South San Francisco, CA 94080  San Mateo County | Major |
| Sunnyvale, City of | Sunnyvale Water Pollution Control Plant | 1444 Borregas Avenue,  Sunnyvale, CA 94089  Santa Clara County | Major |
| U.S. Department of Navy (Treasure Island) | Treasure Island Wastewater Treatment Plant | 1220 Avenue M  San Francisco, CA 94130  San Francisco County | Major |
| Vallejo Sanitation and Flood Control District | Vallejo Sanitation and Flood Control District Wastewater Treatment Plant | 450 Ryder Street  Vallejo, CA 94590  Solano County | Major |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | West County Agency Combined Outfall | 2910 Hilltop Drive  Richmond, CA 94806  Contra Costa County | Major |
| West County Wastewater District Treatment Plant |
| Richmond Municipal Sewer District Water Pollution Control Plant |
| Yountville, Town of | Municipal Wastewater Treatment Plant | 7501 Solano Avenue  Yountville, CA 94599  Napa County | Minor |

Table 1B. Industrial Discharger Information

| **Discharger** | **Name of Facility** | **Facility Address** | **Minor/ Major** |
| --- | --- | --- | --- |
| **Non-Petroleum Refinery** | | | |
| C&H Sugar Company, Inc., and Crockett Community Services District, Crockett Sanitary Department | Joint Use Phillip F. Meads Water Treatment Plant | 830 Loring Avenue  Crockett, CA 94525  Contra Costa County | Major |
| Crockett Cogeneration, LP | Crockett Cogeneration Plant | 550 Loring Avenue  Crockett, CA 94525-1232  Contra Costa County | Minor |
| Eco Services Operations LLC | Eco Services Martinez Plant | 100 Mococo Road  Martinez, CA 94553  Contra Costa County | Major |
| GenOn Delta, LLC | Pittsburg Power Plant | 696 W. 10th Street  Pittsburg, CA 94565  Contra Costa County | Major |
| USS-Posco Industries | Pittsburg Plant | 900 Loveridge Road  Pittsburg, CA 94565  Contra Costa County | Major |
| **Petroleum Refinery** | | | |
| Chevron Products Company | Richmond Refinery | 841 Chevron Way  Richmond, CA 94801  Contra Costa County | Major |
| Phillips 66 (formerly ConocoPhillips) | San Francisco Refinery | 1380 San Pablo Avenue  Rodeo, CA 94572-1354  Contra Costa County | Major |
| Shell Oil Products US and Equilon Enterprises LLC | Shell Martinez Refinery | 3485 Pacheco Blvd  Martinez CA 94553  Contra Costa County | Major |
| Tesoro Refining & Marketing Co. | Golden Eagle Refinery | 150 Solano Way  Martinez, CA 94553  Contra Costa County | Major |
| Valero Refining Company | Valero Benicia Refinery | 3400 East Second Street  Benicia, CA 94510-1005  Solano County | Major |

Table 2A. Discharge Locations

| **Discharger** | **Discharge Point(s)** | **Discharge Point Latitude (North)** | **Discharge Point Longitude (West)** | **Receiving Water** |
| --- | --- | --- | --- | --- |
| American Canyon, City of | 001 | 38.187917º | -122.277139º | North Slough |
| 003 | 38.184917º | -122.279111º | Constructed freshwater wetlands |
| Benicia, City of | 001 | 38.041667º | -122.279111º | Carquinez Strait |
| Burlingame, City of | 002[1] | 37.665278º | -122.361389º | Lower San Francisco Bay |
| Calistoga, City of | 001 | 38.559444 º | -122.557778 º | Napa River |
| 002 | 38.570278º | -122.561111º | Napa River |
| 003 | 38.569341º | -122.556744º | Napa River |
| Central Contra Costa Sanitary District | 001 | 38.045556º | -122.098611º | Suisun Bay |
| Central Marin Sanitation Agency | 001 | 37.948333º | -122.456389º | Central San Francisco Bay |
| Crockett Community Services District | 001 | 38.048611º | -122.182222º | Carquinez Strait |
| Delta Diablo Sanitation District | 001 | 38.027778º | -122.837222º | New York Slough |
| East Bay Dischargers Authority (EBDA); Cities of Hayward and San Leandro; Oro Loma Sanitary District; Castro Valley Sanitary District; Union Sanitary District; Livermore-Amador Valley Water Management Agency; Dublin San Ramon Services District; and City of Livermore | 001 | 37.625556º | -122.130556º | Lower San Francisco Bay |
| East Bay Municipal Utility District | 001 | 37.817222º | -122.348611º | Central San Francisco Bay |
| Fairfield-Suisun Sewer District | 001 | 38.209167º | -122.056667º | Boynton Slough |
| 002 | 38.214444º | -122.065556º | Duck Pond 1 |
| 003 | 38.209722º | -122.058056º | Duck Pond 2 |
| 005 | 38.233333º | -122.058889º | Ledgewood Creek |
| Las Gallinas Valley Sanitary District | 001 | 38.025556º | -122.516111º | Miller Creek |
| 002 | 38.025278º | -122.513333º | Miller Creek |
| Marin County (Paradise Cove), Sanitary District No. 5 of | 001 | 37.897222º | -122.461111º | Central San Francisco Bay |
| Marin County (Tiburon), Sanitary District No. 5 of | 001 | 37.870000º | -122.361389º | Raccoon Strait in Central San Francisco Bay |
| Millbrae, City of | 001 | 37.665278º | -122.361389º | Lower San Francisco Bay |
| Mt. View Sanitary District | 001 | 38.021111º | -122.103611º | Peyton Slough, a tributary to Carquinez Strait |
| Napa Sanitation District | 001 | 38.235833º | -122.286111º | Napa River |
| Novato Sanitary District | 001 | 38.060001º | -122.489995º | San Pablo Bay |
| 002[2] | 38.063333º | -122.510278º | San Pablo Bay |
| Palo Alto, City of | 001 | 37.458333º | -122.110278º | South San Francisco Bay |
| 002 | 37.441667º | -122.112500º | Matedero Creek via Renzel Marsh Pond |
| Petaluma, City of | 001 | 38.209167º | -122.572778º | Petaluma River |
| Pinole, City of | 001 | 38.051667º | -122.270000º | San Pablo Bay |
| Rodeo Sanitary District | 001 | 38.051667º | -122.270000º | San Pablo Bay |
| Saint Helena, City of | 001 | 38.502778º | -122.437500º | Napa River |
| San Francisco (San Francisco International Airport), City and County of | 002[1] | 37.665278º | -122.361389º | Lower San Francisco Bay |
| San Francisco (Southeast Plant), City and County of | 001 | 37.749444º | -122.372778º | Lower San Francisco Bay |
| San Jose and Santa Clara, Cities of | 001 | 37.439722º | -121.958056º | Artesian Slough, a tributary to Coyote Creek and South San Francisco Bay |
| San Mateo, City of | 001 | 37.580556º | -122.245833º | Lower San Francisco Bay |
| Sausalito-Marin City Sanitary District | 001 | 37.843333º | -122.476111º | Central San Francisco Bay |
| Sewerage Agency of Southern Marin | 001 | 37.870000º | -122.451389º | Raccoon Strait in Central San Francisco Bay |
| Silicon Valley Clean Water | 001 | 37.561111º | -122.217222º | Lower San Francisco Bay |
| Sonoma Valley County Sanitary District | 001 | 38.237222º | -122.430833º | Schell Slough, a tributary to the San Pablo Bay |
| South San Francisco and San Bruno, Cities of | 002[1] | 37.665278º | -122.361389º | Lower San Francisco Bay |
| Sunnyvale, City of | 001 | 37.420278º | -122.016667º | Moffett Channel, a tributary to South San Francisco Bay via Guadalupe Slough |
| U.S. Department of Navy (Treasure Island) | 001 | 37.832778º | -122.369444º | Central San Francisco Bay |
| Vallejo Sanitation and Flood Control District | 001 | 38.064722º | -122.228333º | Carquinez Strait |
| 002 | 38.089722º | -122.253333º | Mare Island Strait, a tributary to Carquinez Strait |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | 001 | 37.913056º | -122.418333º | Central San Francisco Bay |
| Yountville, Town of | 001 | 38.406114º | -122.342233º | Napa River |

Footnotes:

[1] These Dischargers share the North Bayside System Unit outfall which serves as combined Discharge Point No. 002 into San Francisco Bay. However, compliance with the requirements of this Order are by each Discharger at its individual compliance station specified in Dischargers’ individual NPDES permits listed in Attachment B of this Order.

[2] Discharge Point No. 002 is subsequent to relocation of discharge to a new San Pablo Bay wetland. The exact location (latitude and longitude) may change slightly from what is indicated in this table.

**Table 2B. Industrial Discharger Location Information**

| **Discharger** | **Discharge Point** | **Discharge Point Latitude** | **Discharge Point Longitude** | **Receiving Water** |
| --- | --- | --- | --- | --- |
| **Industrial Wastewater Discharger (Non-Petroleum Refinery)** | | | | |
| C&H Sugar Company, Inc., and Crockett Community Services District, Crockett Sanitary Dept. | 002 | 38.058333º | -122.224444º | Carquinez Strait |
| Crockett Cogeneration, LP | 001 | 38.056111º | -122.218056º | Carquinez Strait |
| Eco Services Operations LLC | 001 | 38.038333º | -122.116944º | Carquinez Strait |
| GenOn Delta, LLC | 001[1] | 38º 2' 29" | 121º 53' 25" | Suisun Bay |
| USS-Posco Industries | 001 | 38.030000º | -121.86444º | New York Slough |
| 002 | 38.030833º | -121.866110º | New York Slough |
| **Industrial Wastewater Discharger (Petroleum Refinery)** | | | | |
| Chevron Products Company | 001 | 37.970833º | -122.429167º | San Pablo Bay |
| Phillips 66 | 002 | 38.056111º | -122.261430º | San Pablo Bay |
| Shell Oil Products US and Equilon Enterprises LLC | 001 | 38.032222º | -122.128889º | Carquinez Strait |
| Tesoro Refining & Marketing Co. | 001 | 38.048333º | -122.089444º | Suisun Bay |
| Valero Refining Company | 001 | 38.055000º [2] | -122.118611º [2] | Suisun Bay |

Footnote:

[1] This Order applies to the mercury discharges from internal waste streams discharged through these discharge points, and not to the once through cooling water discharges of these discharge points.

[2] Latitude and longitude may change with outfall upgrade as specified in the Discharger’s individual NPDES permit listed in Attachment B of this Order.

Table 3. Administrative Information

|  |  |
| --- | --- |
| This Order was adopted on: | November 8, 2017 |
| This Order shall become effective on: | January 1, 2018 |
| This Order shall expire on: | December 31, 2022 |

I, Bruce H. Wolfe, Executive Officer, do hereby certify that this Order with all attachments is a full, true, and correct copy of the Order adopted by the California Regional Water Quality Control Board, San Francisco BayRegion, on the date indicated above.

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Bruce H. Wolfe**,** Executive Officer

Contents

[I. Facility Information 8](#_Toc488046251)

[II. Findings 8](#_Toc488046252)

[III. Discharge Prohibitions 8](#_Toc488046253)

[IV. Effluent Limitations and Discharge Specifications 9](#_Toc488046254)

[V. Receiving Water Limitations 14](#_Toc488046255)

[VI. Provisions 14](#_Toc488046256)

[A. Standard Provisions 14](#_Toc488046257)

[B. Monitoring and Reporting 15](#_Toc488046258)

[C. Special Provisions 15](#_Toc488046259)

[1. Reopener Provisions 15](#_Toc488046260)

[2. Triggers for Additional Mercury Control 15](#_Toc488046261)

[3. Mercury and PCBs Source Control Program 17](#_Toc488046262)

[4. Risk Reduction Programs 17](#_Toc488046263)

[5. Mercury and PCBs Discharge Adjustments for Recycled Wastewater Use by Industrial Dischargers 18](#_Toc488046264)

[6. PCBs Discharge Adjustment for Urban Stormwater Treatment by Municipal Dischargers 19](#_Toc488046265)

Tables

[Table 1A. Municipal Discharger Information 1](#_Toc487382085)

[Table 2A. Discharge Locations 4](#_Toc487382086)

[Table 3. Administrative Information 6](#_Toc487382087)

[Table 4A. Individual Mercury Effluent Limitations 9](#_Toc487382088)

Attachments

Attachment A – Definitions A-1

Attachment B – Individual NPDES Permit and Order Numbers B-1

Attachment C – Maps of Municipal and Industrial Dischargers C-1

Attachment E – Monitoring and Reporting Program (MRP) E-1

Attachment F – Fact Sheet F-1

# I. Facility Information

Information describing the facilities subject to this Order is summarized in Tables 1A and 1B and in Fact Sheet (Attachment F) sections I and II.

# II. Findings

The California Regional Water Quality Control Board, San Francisco Bay Region (Regional Water Board), finds:

1. **Legal Authorities.** This Order serves as WDRs pursuant to California Water Code article 4, chapter 4, division 7 (commencing with § 13260). This Order is also issued pursuant to federal Clean Water Act (CWA) section 402 and implementing regulations adopted by U.S. EPA and Water Code chapter 5.5, division 7 (commencing with § 13370). It shall serve as a National Pollutant Discharge Elimination System (NPDES) permit for point source discharges of mercury and PCBs from the Dischargers’ facilities listed in Attachment B to surface waters.
2. **Background and Rationale for Requirements.** The Regional Water Board developed the requirements in this Order based on detailed technical analyses which provide the foundation for the Mercury and PCBs TMDL. The Fact Sheet contains background information and rationale for the requirements in this Order and is hereby incorporated into and constitutes findings for this Order. Attachments A through E are also incorporated into this Order.
3. **Provisions and Requirements Implementing State Law.** No provisions or requirements in this Order are included to implement State law only.
4. **Notification of Interested Parties.** The Regional Water Board notified the Dischargers and interested agencies and persons of its intent to prescribe these WDRs and provided an opportunity to submit written comments and recommendations. The Fact Sheet provides details regarding the notification.

**E. Consideration of Public Comment.** The Regional Water Board, in a public meeting, heard and considered all comments pertaining to the discharges. The Fact Sheet provides details regarding the public hearing.

**THEREFORE, IT IS HEREBY ORDERED** that Order No. R2-2012-0096 (previous order) is rescinded upon the effective date of this Order, except for enforcement purposes, and, in order to meet the provisions of Water Code division 7 (commencing with § 13000) and regulations adopted thereunder and the provisions of the CWA and regulations and guidelines adopted thereunder, the Dischargers shall comply with the requirements in this Order. This action in no way prevents the Regional Water Board from taking enforcement action for past violations of the previous order.

# III. Discharge Prohibitions

This Order does not establish additional discharge prohibitions.

# IV. Effluent Limitations and Discharge Specifications

1. **Municipal Discharger Effluent Limitations for Mercury and PCBs.** The Dischargers shall comply with the following mass and concentration effluent limitations at discharge points and monitoring locations specified in Attachment E.

Table 4A. Individual Mercury Effluent Limitations

| **Discharger** | **Average Annual Effluent Limit for Mercury[1] (kg/yr)** | **Average Monthly Effluent Limit for Mercury(µg/L)** | **Average Weekly Effluent Limit for Mercury(µg/L)** |
| --- | --- | --- | --- |
| American Canyon, City of | 0.095 | 0.025 | 0.027 |
| Benicia, City of | 0.088 | 0.066 | 0.072 |
| Burlingame, City of | 0.089 | 0.066 | 0.072 |
| Calistoga, City of | 0.016 | 0.066 | 0.072 |
| Central Contra Costa Sanitary District | 1.3 | 0.066 | 0.072 |
| Central Marin Sanitation Agency | 0.11 | 0.066 | 0.072 |
| Crockett Community Services District, Port Costa Sanitary Dept. | 0.00072 | 0.066 | 0.072 |
| Delta Diablo Sanitation District | 0.19 | 0.066 | 0.072 |
| East Bay Dischargers Authority (EBDA); Cities of Hayward and San Leandro; Oro Loma Sanitary District; Castro Valley Sanitary District; Union Sanitary District; Livermore-Amador Valley Water Management Agency; Dublin San Ramon Services District; and City of Livermore | 2.2 | 0.066 | 0.072 |
| East Bay Municipal Utility District | 1.5 | 0.066 | 0.072 |
| Fairfield-Suisun Sewer District | 0.17 | 0.025 | 0.027 |
| Las Gallinas Valley Sanitary District | 0.10 | 0.066 | 0.072 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | 0.00055 | 0.066 | 0.072 |
| Marin County (Tiburon), Sanitary District No. 5 of | 0.0099 | 0.066 | 0.072 |
| Millbrae, City of | 0.052 | 0.066 | 0.072 |
| Mt. View Sanitary District | 0.034 | 0.025 | 0.027 |
| Napa Sanitation District | 0.17 | 0.066 | 0.072 |
| Novato Sanitary District | 0.079 | 0.066 | 0.072 |
| Palo Alto, City of | 0.31 | 0.025 | 0.027 |
| Petaluma, City of | 0.063 | 0.066 | 0.072 |
| Pinole, City of | 0.055 | 0.066 | 0.072 |
| Rodeo Sanitary District | 0.060 | 0.066 | 0.072 |
| Saint Helena, City of | 0.047 | 0.066 | 0.072 |
| San Francisco (San Francisco International Airport), City and County of | 0.032 | 0.066 | 0.072 |
| San Francisco (Southeast Plant), City and County of | 1.6 | 0.066 | 0.072 |
| San Jose and Santa Clara, Cities of | 0.8 | 0.025 | 0.027 |
| San Mateo, City of | 0.19 | 0.066 | 0.072 |
| Sausalito-Marin City Sanitary District | 0.078 | 0.066 | 0.072 |
| Sewerage Agency of Southern Marin | 0.076 | 0.066 | 0.072 |
| Silicon Valley Clean Water | 0.32 | 0.066 | 0.072 |
| Sonoma Valley County Sanitary District | 0.041 | 0.066 | 0.072 |
| South San Francisco and San Bruno, Cities of | 0.18 | 0.066 | 0.072 |
| Sunnyvale, City of | 0.12 | 0.025 | 0.027 |
| U.S. Department of Navy[2] (Treasure Island) | 0.026 | 0.066 | 0.072 |
| Vallejo Sanitation and Flood Control District | 0.34 | 0.066 | 0.072 |
| West County Agency; West County Wastewater District; City of Richmond; and Richmond Municipal Sewer District No. 1 | 0.23 | 0.066 | 0.072 |
| Yountville, Town of | 0.040 | 0.066 | 0.072 |
| **Aggregate Mass Emission Limit [1],[3] (kg/yr)** | **11** | **Not Applicable** | **Not Applicable** |

Unit Abbreviations:

kg/yr = kilograms per year

µg/L = micrograms per liter

Footnotes:

[1] Compliance with the Average Annual Effluent Limitations is determined annually for each Municipal Discharger each calendar year and is attained if the sum of all individual Municipal Dischargers’ mercury mass emissions, calculated as described below, is not greater than the Aggregate Mass Emission Limit of 11 kg/yr. If the sum of all individual Municipal Dischargers’ mercury mass emission(s) is greater than 11 kg/yr, the Municipal Discharger(s) whose mercury mass emission(s) exceed(s) its (their) individual limitation(s) in Table 4A shall be deemed to be in violation of its (their) mercury mass limitation(s). For compliance determination, mass emissions shall be determined as defined below:

a. The total annual aggregate mass emission shall be the sum of the individual annual mass emissions from each Municipal Discharger. The sum shall be rounded to the nearest kilogram for comparison with the 11 kg/yr.

b. The annual average mass emission for each Discharger shall be computed for the period January 1 through December 31, annually.

c. The annual average mass emission for each Discharger listed in Table 4A above shall be the sum of monthly emissions on a calendar year basis and computed as follows:



or, for Dischargers with less frequent mercury monitoring than monthly, the Annual Mass Emission shall be computed using the arithmetic average of available monthly mass emissions as follows:



where:



and where:

*Ci* = mercury concentration of each individual sample, μg/L

*Qi* = Discharger flow rate on date of sample, millions of gallons per day (MGD)

*N* = number of samples collected during the month

0.003785 = conversion factor to convert (μg/L)\*(MGD) into kg/day

30.5 = number of days in a standard month

0.1154425 = product of (conversion factor)\*(number of standard days per month)

For intermittent Dischargers (Dischargers who do not discharge every day in a calendar month, or who have no discharge for an entire month [Qi = 0]), Qi shall be computed as follows:



where:

*Qd* = total flow for the day when discharge occurred, million gallons

*D* = total number of days where discharge occurred in a month

30.5 = number of days in a standard month

d. The Monthly Mass Emission for a Discharger who provides recycled wastewater for industrial supply shall include the effluent discharge adjustment granted to the Industrial Discharger for its recycled wastewater use as described in Provision VI.C.5 of this Order. The monthly effluent discharge adjustment mass shall be reported in each Self-Monitoring Report and noted in the Annual Report.

[2] This Discharger serves domestic customers but is not a municipal government agency. For the purpose of this Order, this Discharger is a “Municipal Discharger.”

[3] Total differs slightly from the column sum due to rounding to the nearest kilogram.

**Table 4B. Individual PCBs Effluent Limitations**

| **Discharger** | **Average Monthly Effluent Limit for PCBs (µg/L)** | **Maximum Daily Effluent Limit for PCBs (µg/L)** |
| --- | --- | --- |
| American Canyon, City of | 0.00039 | 0.00049 |
| Benicia, City of | 0.012 | 0.017 |
| Burlingame, City of | 0.012 | 0.017 |
| Calistoga, City of | 0.012 | 0.017 |
| Central Contra Costa Sanitary District | 0.012 | 0.017 |
| Central Marin Sanitation Agency | 0.012 | 0.017 |
| Crockett Community Services District, Port Costa Sanitary Dept. | 0.012 | 0.017 |
| Delta Diablo Sanitation District | 0.012 | 0.017 |
| East Bay Dischargers Authority (EBDA); Cities of Hayward and San Leandro; Oro Loma Sanitary District; Castro Valley Sanitary District; Union Sanitary District; Livermore-Amador Valley Water Management Agency; Dublin San Ramon Services District; and City of Livermore | 0.012 | 0.017 |
| East Bay Municipal Utility District | 0.012 | 0.017 |
| Fairfield-Suisun Sewer District | 0.00039 | 0.00049 |
| Las Gallinas Valley Sanitary District | 0.012 | 0.017 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | 0.012 | 0.017 |
| Marin County (Tiburon), Sanitary District No. 5 of | 0.012 | 0.017 |
| Millbrae, City of | 0.012 | 0.017 |
| Mt. View Sanitary District | 0.00039 | 0.00049 |
| Napa Sanitation District | 0.012 | 0.017 |
| Novato Sanitary District | 0.012 | 0.017 |
| Palo Alto, City of | 0.00039 | 0.00049 |
| Petaluma, City of | 0.012 | 0.017 |
| Pinole, City of | 0.012 | 0.017 |
| Rodeo Sanitary District | 0.012 | 0.017 |
| Saint Helena, City of | 0.012 | 0.017 |
| San Francisco (San Francisco International Airport), City and County of | 0.012 | 0.017 |
| San Francisco (Southeast Plant), City and County of | 0.012 | 0.017 |
| San Jose and Santa Clara, Cities of | 0.00039 | 0.00049 |
| San Mateo, City of | 0.012 | 0.017 |
| Sausalito-Marin City Sanitary District | 0.012 | 0.017 |
| Sewerage Agency of Southern Marin | 0.012 | 0.017 |
| Silicon Valley Clean Water | 0.012 | 0.017 |
| Sonoma Valley County Sanitary District | 0.012 | 0.017 |
| South San Francisco and San Bruno, Cities of | 0.012 | 0.017 |
| Sunnyvale, City of | 0.00039 | 0.00049 |
| U.S. Department of Navy (Treasure Island) | 0.012 | 0.017 |
| Vallejo Sanitation and Flood Control District | 0.012 | 0.017 |
| West County Agency; West County Wastewater District; City of Richmond; and Richmond Municipal Sewer District No. 1 | 0.012 | 0.017 |
| Yountville, Town of | 0.012 | 0.017 |

Unit Abbreviation:

µg/L = micrograms per liter

1. **Industrial Discharger Effluent Limitations for Mercury and PCBs.** The Dischargers shall comply with the following mass and concentration effluent limitations at discharge points and monitoring locations specified in Attachment E.

**Table 5A. Individual Mercury Effluent Limitations**

|  |  |  |  |
| --- | --- | --- | --- |
| **Discharger** | **Average Annual Effluent Limit for Mercury[1] (kg/yr)** | **Average Monthly Effluent Limit for Mercury (µg/L)** | **Maximum Daily Effluent Limit for Mercury (µg/L)** |
| **Industrial Dischargers (Non-Petroleum Refinery)** | | | |
| C&H Sugar and Crockett Community Services District, Crockett Sanitary Department | 0.045 | 0.079 | 0.12 |
| Crockett Cogeneration, LP | 0.0047 | 0.079 | 0.12 |
| Eco Services Operations LLC | 0.011 | 0.079 | 0.12 |
| GenOn Delta, LLC | 0.0078 | 0.079 | 0.12 |
| USS-Posco Industries | 0.045 | 0.079 | 0.12 |
| **Industrial Dischargers (Petroleum Refinery)** | | | |
| Chevron Products Company | 0.34 | 0.079 | 0.12 |
| Phillips 66 | 0.13 | 0.079 | 0.12 |
| Shell Oil Products US and Equilon Enterprises LLC | 0.22 | 0.079 | 0.12 |
| Tesoro Refining & Marketing Co. | 0.11 | 0.079 | 0.12 |
| Valero Refining Company | 0.08 | 0.079 | 0.12 |
| **Aggregate Mass Emission Limit[2] (kg/yr)** | **1.0** | **Not Applicable** | **Not Applicable** |

Unit Abbreviations:

kg/yr = kilograms per year

µg/L = micrograms per liter

Footnotes:

[1] Compliance with the Average Annual Effluent Limitations is determined annually for each Industrial Discharger each calendar year and is attained if the sum of all individual Industrial Dischargers’ mercury mass emissions, calculated as described below, is not greater than the Aggregate Mass Emission Limit of 1.0 kg/yr. If the sum of all individual Industrial Dischargers’ mercury mass emission(s) is greater than 1.0 kg/yr, the Industrial Discharger(s) whose mercury mass emission(s) exceed(s) its (their) individual limitation(s) in Table 5A shall be deemed to be in violation of its (their) mercury mass limitation(s). For compliance determination, mass emissions shall be determined as defined below:

a. The total annual aggregate mass emission shall be the sum of the individual annual mass emissions from each Industrial Discharger. The sum shall be rounded to the nearest tenth of a kilogram for comparison with the 1.0 kg/yr.

b. The annual average mass emission for each Discharger shall be computed for the period January 1 through December 31, annually.

c. The annual average mass emission for each Discharger listed in Table 5A above shall be the sum of monthly emissions on a calendar year basis and computed as follows:



or, for Dischargers with less frequent mercury monitoring than monthly, the Annual Mass Emission shall be computed using the arithmetic average of available monthly mass emissions as follows:



where:



and where:

*Ci* = mercury concentration of each individual sample, μg/L

*Qi* = Discharger flow rate on date of sample, millions of gallons per day (MGD)

*N* = number of samples collected during the month

0.003785 = conversion factor to convert (μg/L)\*(MGD) into kg/day

30.5 = number of days in a standard month

0.1154425 = product of (conversion factor)\*(number of standard days per month)

For intermittent Dischargers (Dischargers who do not discharge every day in a calendar month, or who have no discharge for an entire month [Qi = 0]), Qi shall be computed as follows:



where:

*Qd* = total flow for the day when discharge occurred, million gallons

*D* = total number of days where discharge occurred in a month

30.5 = number of days in a standard month

d. For an Industrial Discharger who uses treated recycled wastewater for industrial supply from a Municipal Discharger named in this Order, the Industrial Discharger shall subtract from its Monthly Mass Emission in c., above, an adjustment for the recycled water used and discharged through its discharge point as provided in Provision VI.C.5 of this Order. The Industrial Discharger shall report this effluent discharge adjustment mass to the Municipal Discharger that provided the recycled wastewater within 15 days following the end of the calendar month for which an adjustment is applied and shall report the adjustment in each Self-Monitoring Report and in its Annual Report.

[2] Total differs slightly from the column sum due to rounding to the nearest kilogram.

**Table 5B. Individual PCBs Effluent Limitations**

|  |  |  |
| --- | --- | --- |
| **Discharger** | **Average Monthly Effluent Limit for PCBs (µg/L)** | **Maximum Daily Effluent Limit for PCBs (µg/L)** |
| **Industrial Dischargers (Non-Petroleum Refinery)** | | |
| C&H Sugar and Crockett Community Services District, Crockett Sanitary Department | 0.012 | 0.018 |
| Eco Services Operations LLC | 0.012 | 0.018 |
| USS-Posco Industries | 0.012 | 0.018 |
| **Industrial Dischargers (Petroleum Refinery)** | | |
| Chevron Products Company | 0.00095 | 0.0015 |
| Phillips 66 | 0.00095 | 0.0015 |
| Shell Oil Products US and Equilon Enterprises LLC | 0.00095 | 0.0015 |
| Tesoro Refining & Marketing Co. | 0.00095 | 0.0015 |
| Valero Refining Company | 0.00095 | 0.0015 |

Unit Abbreviation:

µg/L = micrograms per liter

# V. Receiving Water Limitations

This Order continues receiving water limitations that are specified in the individual NPDES permits listed in Attachment B.

# VI. Provisions

## A. Standard Provisions

Dischargers shall comply with the Federal and Regional Standard Provisions included in Attachments D and G, as amended, of their individual NPDES permits listed in Attachment B of this Order.

## B. Monitoring and Reporting

Dischargers shall comply with the MRP (Attachment E) and future revisions thereto and applicable sampling and reporting requirements in Attachments D and G, as amended, of their individual NPDES permits listed in Attachment B of this Order.

## Special Provisions

### 1. Reopener Provisions

The Regional Water Board may modify or reopen this Order prior to its expiration date if there is modification of the San Francisco Bay Mercury or PCBs TMDL implementation provisions.

### 2. Triggers for Additional Mercury Control

**a.** Each individual Discharger shall comply with the tasks specified in C.2.c. of this Order if its discharge exceeds any of the applicable mercury triggers described in Tables 6 and 7.

**Table 6. Mercury Triggers for Municipal Dischargers**

|  |  |  |
| --- | --- | --- |
| **Type of Trigger** | **Average Monthly** | **Maximum Daily** |
| Concentration of Mercury in Discharge for Secondary Treatment Plants | 0.041 μg/L | 0.065 μg/L |
| Concentration of Mercury in Discharge for Advanced Secondary Treatment Plants | 0.011 μg/L | 0.021 μg/L |
| Mass Emission of Mercury in Discharge | Individual annual mass emission limit, as depicted in Table 4A, above, and computed as a 12-month running average, as shown in C.2.b., below. | |

Unit Abbreviation:

µg/L = micrograms per liter

**Table 7. Mercury Triggers for Industrial Dischargers**

|  |  |  |
| --- | --- | --- |
| **Type of Trigger** | **Average Monthly** | **Maximum Daily** |
| Concentration of Mercury in Discharge | 0.037 μg/L | 0.062 μg/L |
| Mass Emission of Mercury in Discharge | Individual annual mass emission limit, as depicted in Table 5A, above, and computed as a 12-month running average, as shown in C.2.b., below. | |

Unit Abbreviation:

µg/L = micrograms per liter

**b.** The running 12-month average mercury mass emission shall be calculated monthly for each calendar month as follows:

where the current mass emission is the monthly mass emission for the current calendar month computed as shown in Effluent Limitations and Discharge Specifications IV.A, footnote c above.

**c.** Each Discharger who exceeds any of the applicable triggers for mercury listed in Table 6 or 7, above, shall comply with the following action requirements:

**Table 8. Action Plan Required in Response to Mercury Trigger Exceedance**

| **Task** | **Deadline** |
| --- | --- |
| **i.** ***Accelerated Sampling.*** As soon as the Discharger becomes aware of an exceedance of a mercury trigger, resample within 48 hours and commence at minimum weekly sampling for a total of at least 6 new samples. If all 6 new samples show mercury levels below the triggers, return to routine sampling. If during the accelerated sampling, (1) any of the new samples are above the maximum daily trigger, or (2) the monthly average of the new samples is above the monthly trigger, or (3) the 12-month running average mass is above the mass trigger, then proceed with an action plan for mercury reduction and continue sampling monthly until the observed mercury discharge is below the trigger levels for 3 consecutive months, at which point the Discharger shall complete the reporting of this exceedance as required by tasks ii and iv, below, and return to routine monitoring, and discontinue efforts under task iii, below. | See deadlines in task description. |
| **ii. *Report Trigger Exceedance.*** Report to the Regional Water Board any exceedance of mercury trigger levels in the cover letter of its Self‑Monitoring Report and the status of its plans and actions to accelerate monitoring and/or develop and implement an action plan for mercury reduction. | In the Self-Monitoring Report due 30 days after the end of the monitoring period. |
| **iii.** ***Action Plan for Mercury Reduction*.** Develop, submit, and implement an Action Plan that (1) evaluates the cause1 of the trigger exceedance(s); (2) evaluates the effectiveness of existing pollution prevention or pretreatment programs and methods for preventing future exceedances; (3) evaluates the feasibility and effectiveness of technology enhancements to improve treatment plant performance; and (4) evaluates other measures for preventing future exceedances. In addition, the Discharger shall identify in the Action Plan mercury reduction measures it will take along with an implementation schedule for those measures to correct current and prevent future trigger exceedances.  1 *Possible causes of exceedances include (but are not limited to) changes in reclamation; increases in the number of sewer connections, increases in infiltration and inflow (I/I); changes in the type or number of industrial, commercial, or residential sources; changes in the raw material used in manufacturing processes; changes in treatment system operation; or factors beyond the Discharger’s control, such as a natural disaster, vandalism, illegal dumping, or extreme flood event.* | Within 130 days of the initial trigger exceedance. |
| **iv.** ***Annual Reporting*.** Provide a status of its mercury reduction efforts in the annual Self-Monitoring Report. Additionally, as causes and corrective actions are identified, the Discharger shall amend or supplement its Action Plan as appropriate. Such changes shall be reported to the Regional Water Board in the Discharger’s Annual Self-Monitoring Report. | Annually due February 1 of each year until the Discharger demonstrates compliance with trigger levels for a continuous 3-month period of sampling. |

### 3. Mercury and PCBs Source Control Program

Each Discharger shall evaluate whether there are controllable sources of mercury or PCBs to its wastewater system (e.g., PCBs-containing industrial equipment for PCBs, discharges from amalgam-generating dental practices for mercury). The Discharger shall continue to implement and look for opportunities to improve existing measures to control such sources. Each Discharger shall submit the results of this evaluation, including any proposed control actions and implementation schedules, in its annual pollution prevention reports required by its individual NPDES permit.

### 4. Risk Reduction Programs

Each Discharger shall continue to implement and participate in programs to reduce mercury and PCBs-related risks to humans from consumption of San Francisco Bay and Sacramento‑San Joaquin River Delta fish. This requirement may be satisfied by a combination of related efforts through the Regional Monitoring Program or other similar collaborative efforts. Each Discharger shall describe the progress of its efforts in its Annual Self-Monitoring Report. Alternatively, the Bay Area Clean Water Agencies (BACWA) may fulfill the annual reporting requirement by providing a summary of annual risk reduction program efforts for agencies that choose to participate through BACWA.

### 5. Mercury and PCBs Discharge Adjustments for Recycled Wastewater Use by Industrial Dischargers

When an Industrial Discharger named on Table 1B of this Order uses recycled wastewater from a Municipal Discharger named on Table 1A of this Order, the Industrial Discharger may, at its option, apply discharge adjustments (hereinafter Mercury or PCBs Adjustment) to its mercury or PCBs discharge concentration or mercury mass emission to be subtracted from the final discharge concentration or mass emission when determining compliance with its concentration and mass limits specified in Tables 5A and 5B of this Order. The Mercury or PCBs Adjustments shall be based on measured influent mercury and PCBs levels from the recycled wastewater in accordance with the following:

**a.** **Monitoring Frequencies.** The Industrial Discharger shall sample and analyze the influent recycled wastewater and the effluent discharge at least monthly for mercury and quarterly for PCBs. Influent sampling shall include measurement of daily flow volume for the entire duration that Mercury or PCBs Adjustments are applied. Influent sampling shall occur at an appropriate influent sampling station as identified in the Discharger’s individual permit.

**b.** **Time Intervals between Influent and Effluent Sampling.** The Industrial Discharger shall determine the time interval (i.e., lag time) between sampling a given constituent of concern in the influent recycled water and sampling the same water for the constituent when it appears in the final effluent. The basis for this determination must be included in any calculation of Mercury or PCBs Adjustments.

**c. Adjustment Calculation Procedure.**

* + 1. **Concentration Adjustment.** The Mercury or PCBs Adjustment for concentration shall be calculated as follows:

where

*Ci* = Recycled water influent mercury or PCBs concentration, μg/L

*Cp* =Potable water influent mercury or PCBs concentration, μg/L

*Qt* = Total influent recycled water flow volume corresponding to the appropriate monitoring period (e.g., monthly flow volume for mercury, quarterly flow volume for PCBs), million gallons

*Qy* = Total effluent flow volume corresponding to the appropriate monitoring period and lag time (e.g.,Y days) after influent is sampled, million gallons

Example: Mercury is monitored monthly. The lag time is Y days.

Step 1: {(influent concentration of mercury in recycled wastewater, *C2i*) – (influent concentration of mercury in potable water, *C1i*)} x (total influent volume of recycled wastewater for the month, *Qt*) = (influent mass of mercury from recycled wastewater)

Step 2: (influent mass) ÷ (total effluent discharge volume for the 30-day period, Y days after influent sampled, *Qy*) = (Mercury Adjustment to be subtracted from concentration of mercury in the discharge, valid for that month)

1. **Mass Adjustment.** The Mercury or PCBs Adjustment for mass shall be calculated as follows:

where

*Ci* = Recycled water influent mercury or PCBs concentration, μg/L

*Cp* = Potable water influent mercury or PCBs concentration, μg/L

*Qt* = Total influent recycled water flow volume corresponding to the appropriate monitoring period (e.g., monthly [30.5 days] flow volume for mercury, quarterly [90 days] flow volume for PCBs), million gallons

*Dt* = Total number of days in the appropriate monitoring period

Example: Mercury is monitored monthly. The lag time is Y days.

Step 1 :{(influent concentration of mercury in recycled wastewater, *C2i*) – (influent concentration of mercury in potable water, *C1i*)} x (total influent volume of recycled wastewater for the month, *Qt*) = (influent mass of mercury from recycled wastewater)

Step 2: (influent mass) ÷ (30.5, the number of days in a standard month, *Dt*) = (Mercury Adjustment to be subtracted from monthly mass emission, valid for that month)

**d. Effluent Limit Exceedance.**  If an Industrial Discharger opts to apply a Mass Adjustment, the Regional Water Board shall transfer that adjustment to the mass emission for the corresponding discharge interval from the Municipal Discharger who is the producer and source of the recycled wastewater. If this reverse adjustment results in an adjusted mass discharge level above both of the following criteria, then that Municipal Discharger is in violation of its Annual Average Effluent Limit and is subject to enforcement action by the Regional Water Board:

1. **Individual Mass Adjustment.** The sum of the adjusted mass discharge levels from the Industrial Discharger and the Municipal Discharger exceeds the sum of the individual Average Annual Effluent Limits for these two Dischargers; and
2. **Aggregate Mass Adjustment.** The adjusted mass discharge levels from the Municipal Discharger results in an aggregate mass emission from all Municipal Dischargers that exceeds the Aggregate Mass Emission Limit for Municipal Dischargers.

### 6. PCBs Discharge Adjustment for Urban Stormwater Treatment by Municipal Dischargers

When a Municipal Discharger named on Table 1A of this Order accepts and treats urban runoff that is diverted from municipal separate storm sewer systems to all or parts of its wastewater treatment facility, the Municipal Discharger may, at its option, apply an adjustment (hereinafter Runoff Adjustment) to its PCBs discharge concentration when determining compliance with its concentration limits specified in Table 4B, provided that the total mass used in Runoff Adjustments from all Municipal Dischargers does not exceed 1.0 kg/year. The Runoff Adjustment shall be based on measured influent PCBs levels from urban runoff in accordance with the following:

### a. Representative Samples. The Municipal Discharger shall have data from a representative sample or samples of the urban runoff targeted for diversion. Separate sampling will be necessary to characterize dry weather diversions and wet weather diversions. The Discharger shall measure daily flow volumes for the entire duration that the Runoff Adjustment is to be applied. The Discharger shall measure these flows at an appropriate influent sampling station as identified in the Discharger’s individual permit and shall categorize each diversion as a dry weather diversion or a wet weather diversion.

**b. Adjustment Calculation Procedure.** The PCBs Runoff Adjustment shall be calculated as follows:

where

*Cdi* = Dry weather urban runoff influent PCBs concentration, μg/L

*Qdr* = Total dry weather influent urban runoff flow volume corresponding to the appropriate monitoring period (e.g., quarterly [90 days] or semi-annual [180 days] flow volume), million gallons

*Cwi* = Wet weather urban runoff influent PCBs concentration, μg/L

*Qwr* = Total wet weather influent urban runoff flow volume corresponding to the appropriate monitoring period (e.g., quarterly [90 days] or semi-annual [180 days] flow volume), million gallons

*Qt* = Total effluent flow volume corresponding to the appropriate monitoring period, million gallons

Example: PCBs is monitored quarterly.

Step 1 :{(influent urban runoff concentration of PCBs in dry weather, *Cdi*) x (total influent urban runoff volume of dry weather diversion for the quarter, *Qdr*) + (influent urban runoff concentration of PCBs in wet weather, *Cwi*) x (total influent urban runoff volume of wet weather diversion for the quarter, *Qwr*)} = (influent mass of PCBs from urban runoff)

Step 2: (influent mass) ÷ (total effluent discharge volume for the 90-day period, *Qt*) = (Runoff Adjustment to be subtracted from the concentration of PCBs, valid for that quarter)

Attachment A – Definitions

Arithmetic Mean (μ)

Also called the average, the sum of measured values divided by the number of samples. For ambient water concentrations, the arithmetic mean is calculated as follows:

Arithmetic mean = μ = Σx / n where: Σx is the sum of the measured ambient water concentrations, and n is the number of samples.

Average Monthly Effluent Limitation (AMEL)

The highest allowable average of daily discharges over a calendar month, calculated as the sum of all daily discharges measured during a calendar month divided by the number of daily discharges measured during that month.

Average Weekly Effluent Limitation (AWEL)

The highest allowable average of daily discharges over a calendar week (Sunday through Saturday), calculated as the sum of all daily discharges measured during a calendar week divided by the number of daily discharges measured during that week.

Bioaccumulative

Taken up by an organism from its surrounding medium through gill membranes, epithelial tissue, or from food and subsequently concentrated and retained in the body of the organism.

Carcinogenic

Known to cause cancer in living organisms.

Coefficient of Variation

Measure of data variability calculated as the estimated standard deviation divided by the arithmetic mean of the observed values.

Daily Discharge

Either: (1) the total mass of the constituent discharged over the calendar day (12:00 am through 11:59 pm) or any 24-hour period that reasonably represents a calendar day for purposes of sampling (as specified in the permit) for a constituent with limitations expressed in units of mass; or (2) the unweighted arithmetic mean measurement of the constituent over the day for a constituent with limitations expressed in other units of measurement (e.g., concentration).

The daily discharge may be determined by the analytical results of a composite sample taken over the course of one day (a calendar day or other 24-hour period defined as a day) or by the arithmetic mean of analytical results from one or more grab samples taken over the course of the day.

For composite sampling, if 1 day is defined as a 24-hour period other than a calendar day, the analytical result for the 24-hour period is considered the result for the calendar day in which the 24-hour period ends.

Detected, but Not Quantified (DNQ)

Sample result less than the RL, but greater than or equal to the laboratory’s MDL. Sample results reported as DNQ are estimated concentrations.

Dilution Credit

Amount of dilution granted to a discharge in the calculation of a water quality-based effluent limitation, based on the allowance of a specified mixing zone. It is calculated from the dilution ratio or determined by conducting a mixing zone study or modeling the discharge and receiving water.

Effluent Concentration Allowance (ECA)

Value derived from the water quality criterion/objective, dilution credit, and ambient background concentration that is used, in conjunction with the CV for the effluent monitoring data, to calculate a long-term average (LTA) discharge concentration. The ECA has the same meaning as wasteload allocation (WLA) as used in U.S. EPA guidance (*Technical Support Document For Water Quality-based Toxics Control*, March 1991, second printing, EPA/505/2-90-001).

Enclosed Bay

Indentation along the coast that encloses an area of oceanic water within a distinct headlands or harbor works. Enclosed bays include all bays where the narrowest distance between the headlands or outermost harbor works is less than 75 percent of the greatest dimension of the enclosed portion of the bay. Enclosed bays include, but are not limited to, Humboldt Bay, Bodega Harbor, Tomales Bay, Drake’s Estero, San Francisco Bay, Morro Bay, Los Angeles-Long Beach Harbor, Upper and Lower Newport Bay, Mission Bay, and San Diego Bay. Enclosed bays do not include inland surface waters or ocean waters.

Estimated Chemical Concentration

Concentration that results from the confirmed detection of the substance below the ML value by the analytical method.

Estuaries

Waters, including coastal lagoons, located at the mouths of streams that serve as areas of mixing for fresh and ocean waters. Coastal lagoons and mouths of streams that are temporarily separated from the ocean by sandbars are considered estuaries. Estuarine waters are considered to extend from a bay or the open ocean to a point upstream where there is no significant mixing of fresh water and seawater. Estuarine waters include, but are not limited to, the Sacramento-San Joaquin Delta, as defined in Water Code section 12220, Suisun Bay, Carquinez Strait downstream to the Carquinez Bridge, and appropriate areas of the Smith, Mad, Eel, Noyo, Russian, Klamath, San Diego, and Otay rivers. Estuaries do not include inland surface waters or ocean waters.

Inland Surface Waters

All surface waters of the state that do not include the ocean, enclosed bays, or estuaries.

Instantaneous Maximum Effluent Limitation

Highest allowable value for any single grab sample or aliquot (i.e., each grab sample or aliquot is independently compared to the instantaneous maximum limitation).

Instantaneous Minimum Effluent Limitation

Lowest allowable value for any single grab sample or aliquot (i.e., each grab sample or aliquot is independently compared to the instantaneous minimum limitation).

Maximum Daily Effluent Limitation (MDEL)

Highest allowable daily discharge of a pollutant, over a calendar day (or 24-hour period). For pollutants with limitations expressed in units of mass, the daily discharge is calculated as the total mass of the pollutant discharged over the day. For pollutants with limitations expressed in other units of measurement, the daily discharge is calculated as the arithmetic mean measurement of the pollutant over the day.

Median

Middle measurement in a set of data. The median of a set of data is found by first arranging the measurements in order of magnitude (either increasing or decreasing order). If the number of measurements (n) is odd, then the median = X(n+1)/2. If n is even, then the median = (Xn/2 + X(n/2)+1)/2 (i.e., the midpoint between n/2 and n/2+1).

Method Detection Limit (MDL)

Minimum concentration of a substance that can be measured and reported with 99 percent confidence that the analyte concentration is greater than zero, as defined in in 40 C.F.R. part 136, Attachment B, revised as of July 3, 1999.

Minimum Level (ML)

Concentration at which the entire analytical system gives a recognizable signal and acceptable calibration point. The ML is the concentration in a sample that is equivalent to the concentration of the lowest calibration standard analyzed by a specific analytical procedure, assuming that all the method specified sample weights, volumes, and processing steps have been followed.

Mixing Zone

Limited volume of receiving water allocated for mixing with a wastewater discharge where water quality criteria can be exceeded without causing adverse effects to the overall water body.

Not Detected (ND)

Sample results less than the laboratory’s MDL.

Persistent Pollutants

Substances for which degradation or decomposition in the environment is nonexistent or very slow.

Pollutant Minimization Program

Program of waste minimization and pollution prevention actions that include, but are not limited to, product substitution, waste stream recycling, alternative waste management methods, and education of the public and businesses. The goal of the Pollutant Minimization Program is to reduce all potential sources of a priority pollutant through pollutant minimization (control) strategies, including pollution prevention measures as appropriate, to maintain the effluent concentration at or below the water quality-based effluent limitation. Pollution prevention measures may be particularly appropriate for persistent bioaccumulative priority pollutants where there is evidence that beneficial uses are being impacted. Cost effectiveness may be considered when establishing the requirements of a Pollutant Minimization Program. The completion and implementation of a Pollution Prevention Plan, if required pursuant to Water Code section 13263.3(d), is considered to fulfill Pollutant Minimization Program requirements.

Pollution Prevention

Any action that causes a net reduction in the use or generation of a hazardous substance or other pollutant that is discharged into water and includes, but is not limited to, input change, operational improvement, production process change, and product reformulation (as defined in Water Code section 13263.3). Pollution prevention does not include actions that merely shift a pollutant in wastewater from one environmental medium to another environmental medium, unless clear environmental benefits of such an approach are identified to the satisfaction of the State Water Board or Regional Water Board.

Reporting Level (RL)

ML (and its associated analytical method) chosen by the Discharger for reporting and compliance determination from the MLs included in this Order, including an additional factor if applicable as discussed herein. The MLs included in this Order correspond to approved analytical methods for reporting a sample result that are selected by the Regional Water Board either from SIP Appendix 4 in accordance with SIP section 2.4.2 or established in accordance with SIP section 2.4.3. The ML is based on the proper application of method-based analytical procedures for sample preparation and the absence of any matrix interferences. Other factors may be applied to the ML depending on the specific sample preparation steps employed. For example, the treatment typically applied in cases where there are matrix-effects is to dilute the sample or sample aliquot by a factor of ten. In such cases, this additional factor must be applied to the ML in the computation of the RL.

Source of Drinking Water

Any water designated as having a municipal or domestic supply (MUN) beneficial use.

Standard Deviation (σ)

Measure of variability calculated as follows:

σ = (∑[(x - μ)2]/(n – 1))0.5

where:

x is the observed value;

μ is the arithmetic mean of the observed values; and

n is the number of samples.

Toxicity Reduction Evaluation (TRE)

Study conducted in a step-wise process designed to identify the causative agents of effluent or ambient toxicity, isolate the sources of toxicity, evaluate the effectiveness of toxicity control options, and then confirm the reduction in toxicity. The first steps of the TRE consist of the collection of data relevant to the toxicity, including additional toxicity testing, and an evaluation of facility operations and maintenance practices, and best management practices. A Toxicity Identification Evaluation (TIE) may be required as part of the TRE, if appropriate. A TIE is a set of procedures to identify the specific chemicals responsible for toxicity. These procedures are performed in three phases (characterization, identification, and confirmation) using aquatic organism toxicity tests.

1. B


ATTACHMENT B – INDIVIDUAL NPDES PERMIT AND ORDER NUMBERS


| **Discharger** | **NPDES Permit No.** | **Existing Order No.[1]** | **Existing Order Adoption Date** | **Existing Order Expiration Date** |
| --- | --- | --- | --- | --- |
| **Municipal Dischargers** | | | | |
| American Canyon, City of | CA0038768 | R2-2017-0008 | 4/12/2017 | 5/31/2022 |
| Benicia, City of | CA0038091 | R2-2014-0023 | 6/11/2014 | 7/31/2019 |
| Burlingame, City of | CA0037788 | R2-2013-0015 | 5/8/2013 | 6/30/2018 |
| Calistoga, City of | CA0037966 | R2-2016-0018 | 4/13/2016 | 4/30/2021 |
| Central Contra Costa Sanitary District | CA0037648 | R2-2017-0009 | 4/12/2017 | 5/31/2022 |
| Central Marin Sanitation Agency | CA0038628 | R2-2012-0051 | 6/13/2012 | 7/31/2017 |
| Crockett Community Services District, Port Costa Sanitary Dept. | CA0037885 | R2-2013-0035 | 10/9/2013 | 11/30/2018 |
| Delta Diablo Sanitation District | CA0038547 | R2-2014-0030 | 8/13/2014 | 9/30/2019 |
| East Bay Dischargers Authority | CA0037869 | R2-2017-0016 | 5/10/2017 | 6/30/2022 |
| Union S.D. Wet Weather Outfall | CA0038733 | R2-2015-0045 | 11/18/2015 | 12/31/2020 |
| Union S.D. Hayward Marsh | CA0038636 | R2-2011-0058 | 9/14/2011 | 10/31/2016 |
| Dublin San Ramon Services District | CA0037613 | R2-2017-0017 | 5/10/2017 | 6/30/2022 |
| City of Livermore | CA0038008 | R2-2017-0018 | 5/10/2017 | 6/30/2022 |
| LAVWMA Wet Weather Outfall | CA0038679 | R2-2016-0015 | 4/13/2016 | 5/31/2021 |
| East Bay Municipal Utility District | CA0037702 | R2-2015-0018 | 5/13/2015 | 6/30/2020 |
| Fairfield-Suisun Sewer District | CA0038024 | R2-2015-0013 | 3/11/2015 | 4/30/2020 |
| Las Gallinas Valley Sanitary District | CA0037851 | R2-2015-0021 | 5/13/2015 | 6/30/2020 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | CA0037427 | R2-2016-0042 | 10/12/2016 | 11/30/2021 |
| Marin County (Tiburon), Sanitary District No. 5 of | CA0037753 | R2-2013-0027 | 8/14/2013 | 9/30/2018 |
| Millbrae, City of | CA0037532 | R2-2013-0037 | 12/11/2013 | 1/31/2019 |
| Mt. View Sanitary District | CA0037770 | R2-2016-0023 | 5/11/2016 | 6/30/2021 |
| Napa Sanitation District | CA0037575 | R2-2016-0035 | 7/13/2016 | 8/31/2021 |
| Novato Sanitary District | CA0037958 | R2-2015-0034 | 7/8/2015 | 8/31/2020 |
| Palo Alto, City of | CA0037834 | R2-2014-0024 | 6/11/2014 | 7/31/2019 |
| Petaluma, City of | CA0037810 | R2-2016-0014 | 4/13/2016 | 5/31/2021 |
| Pinole, City of | CA0037796 | R2-2012-0059 | 8/8/2012 | 9/30/2017 |
| Rodeo Sanitary District | CA0037826 | R2-2012-0027 | 4/11/2012 | 5/31/2017 |
| Saint Helena, City of | CA0038016 | R2-2016-0003 | 1/13/2016 | 2/28/2021 |
| San Francisco (San Francisco International Airport), City and County of | CA0038318 | R2-2013-0011 | 5/8/2013 | 6/30/2018 |
| San Francisco (Southeast Plant), City and County of | CA0037664 | R2-2013-0029 | 8/14/2013 | 9/30/2018 |
| San Jose and Santa Clara, Cities of | CA0037842 | R2-2014-0034 | 9/10/2014 | 10/31/2019 |
| San Mateo, City of | CA0037541 | R2-2013-0006 | 3/13/2013 | 4/30/2018 |
| Sausalito-Marin City Sanitary District | CA0038067 | R2-2012-0083 | 11/14/2012 | 12/31/2017 |
| Sewerage Agency of Southern Marin | CA0037711 | R2-2012-0094 | 12/12/2012 | 1/31/2018 |
| Silicon Valley Clean Water | CA0038369 | R2-2012-0062 | 8/8/2012 | 9/30/2017 |
| Sonoma Valley County Sanitary District | CA0037800 | R2-2014-0020 | 5/14/2014 | 6/30/2019 |
| South San Francisco and San Bruno, Cities of | CA0038130 | R2-2014-0012 | 4/9/2014 | 5/31/2019 |
| Sunnyvale, City of | CA0037621 | R2-2014-0035 | 9/10/2014 | 10/31/2019 |
| U.S. Department of Navy, Treasure Island | CA0110116 | R2-2015-0004 | 1/21/2015 | 3/31/2020 |
| Vallejo Sanitation and Flood Control District | CA0037699 | R2-2012-0017 | 2/8/2012 | 3/31/2017 |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | CA0038539 | R2-2013-0016 | 5/8/2013 | 6/30/2018 |
| Yountville, Town of | CA0038121 | R2-2015-0029 | 6/10/2015 | 7/31/2020 |
| **Industrial Dischargers (Non-Petroleum Refinery)** | | | | |
| C&H Sugar and Crockett Community Services District, Crockett Sanitary Dept. | CA0005240 | R2-2012-0084 | 11/14/12 | 12/31/17 |
| Crockett Cogeneration, LP, and Pacific Crockett Energy, Inc. | CA0029904 | R2-2016-0022 | 5/11/2016 | 6/30/2021 |
| Eco Services Operations LLC | CA0006165 | R2-2015-0052 | 12/16/2015 | 1/31/2021 |
| GenOn Delta, LLC | CA0004880 | R2-2002-0072 | 6/19/02 | 5/31/07 |
| USS-Posco Industries | CA0005002 | R2-2016-0043 | 11/9/2016 | 12/31/2021 |
| **Industrial Dischargers (Petroleum Refinery)** | | | | |
| Chevron Products Company | CA0005134 | R2-2016-0047 | 12/14/2016 | 1/31/2022 |
| Phillips 66 | CA0005053 | R2-2016-0044 | 11/9/2016 | 12/31/2021 |
| Shell Oil Products US and Equilon Enterprises LLC | CA0005789 | R2-2012-0052 | 6/13/2012 | 7/31/2017 |
| Tesoro Refining & Marketing Co. | CA0004961 | R2-2015-0033 | 7/8/2015 | 8/31/2020 |
| Valero Refining Company | CA0005550 | R2-2015-0037 | 8/12/2015 | 9/30/2020 |

Footnote:

[1] The orders shown are for the primary permit reissuance and do not include permit amendments.

**CATTACHMENT C – MAPS OF MUNICIPAL AND INDUSTRIAL DISCHARGERS**





1. E

ATTACHMENT E – MONITORING AND REPORTING PROGRAM (MRP)

Contents

[I. General Monitoring Provisions E-2](#_Toc487612916)

[II. Monitoring Locations E-3](#_Toc487612917)

[III. Effluent Monitoring Requirements E-3](#_Toc487612918)

[IV. Reporting Requirements E-4](#_Toc487612919)

[A. General Monitoring and Reporting Requirements E-4](#_Toc487612920)

[B. Individual Reporting in Self-Monitoring Reports (SMRs) E-4](#_Toc487612921)

[C. Discharge Monitoring Reports (DMRs) E-7](#_Toc487612923)

Tables

[Table E-1. Minimum Levels E-2](#_Toc488046594)

[Table E-2. Monitoring Locations E-3](#_Toc488046595)

[Table E-3. Effluent Monitoring E-3](#_Toc488046596)

[Table E-4. Monitoring Periods E-5](#_Toc488046597)

[Table E-5. U.S. EPA Method 1668C Qualifiers in CIWQS E-6](#_Toc488046598)

ATTACHMENT E – MONITORING AND REPORTING PROGRAM (MRP)

Clean Water Act section 308 and 40 C.F.R. sections 122.41(h), 122.41(j)-(l), 122.44(i), and 122.48 require that all NPDES permits specify monitoring and reporting requirements. Water Code sections 13267 and 13383 also authorize the Regional Water Board to establish monitoring, inspection, entry, reporting, and recordkeeping requirements. This MRP establishes monitoring, reporting, and recordkeeping requirements that implement federal and State laws and regulations.

I. General Monitoring Provisions

**A.** Dischargers shall comply with this MRP. The Executive Officer may amend this MRP pursuant to 40 C.F.R. sections 122.62, 122.63, and 124.5. If any discrepancies exist between this MRP and the “Regional Standard Provisions, and Monitoring and Reporting Requirements (Supplement to Attachment D) for NPDES Wastewater Discharge Permits” (Attachment G) in the individual permits listed in Attachment B of this Order, this MRP shall prevail.

**B.** Sampling is required during the entire year when discharging. Dischargers shall conduct all monitoring in accordance with Attachment D, section III, as supplemented by Attachment G, of their individual permits listed in Attachment B of this Order. Equivalent test methods must be more sensitive than those specified in 40 C.F.R. section 136 and must be specified in this permit.

**C.** For compliance monitoring, analyses shall be conducted using the lowest commercially available and reasonably achievable detection levels. The objective is to provide quantification of constituents sufficient to allow evaluation of observed concentrations with respect to the Minimum Levels given below. All Minimum Levels are expressed as µg/L, equivalent to parts per billion (ppb). According to the SIP, method-specific factors can be applied. In such cases, this additional factor must be applied in the computation of the Reporting Level. Application of such factors will alter the Reporting Level from the Minimum Level for the analysis. Dischargers are to instruct laboratories to establish calibration standards so that the Minimum Level value is the lowest calibration standard. At no time is a Discharger to use analytical data derived from extrapolation beyond the lowest point of the calibration curve. The E-1 below indicates the highest minimum level that the Discharger’s laboratory must achieve for calibration purposes.

Table E-1. Minimum Levels

|  |  |  |
| --- | --- | --- |
| **Constituent** | **Minimum Level** | **Units** |
| Mercury | 0.0005 | μg/L |
| PCB 1016, 1221, 1232, 1242, 1248, 1254, 1260 | 0.5 | μg/L |

II. Monitoring Locations

Dischargers shall establish the following monitoring locations to demonstrate compliance with the effluent limitations, discharge specifications, and other requirements in this Order:

Table E-2. Monitoring Locations

| Sampling Location Type | Monitoring  Location Name [1] | Monitoring Location Description |
| --- | --- | --- |
| Effluent | Individual monitoring locations for discharges of treated wastewater (normally EFF-001) are specified in the MRP of Dischargers’ individual NPDES permits listed in Attachment B of this Order. | Individual monitoring location descriptions are described in the MRP of Dischargers’ individual NPDES permits listed in Attachment B of this Order. |

Footnotes:

[1] For San Francisco International Airport, the monitoring location is EFF-001A for both its sanitary and industrial plants.

For the City of Calistoga, annual monitoring shall alternate each year between EFF-001 and EFF-002.

For C&H Sugar Company, Inc., the monitoring location is EFF-002.

For GenOn Delta, LLC, the monitoring locations are E-001B through to and including E-001I.

III. Effluent Monitoring Requirements

The Dischargers shall monitor their individual treatment plant effluent for mercury and PCBs as follows:

Table E-3. Effluent Monitoring

| **Parameter** | **Units** | **Sample Type** [1] | **Minimum Sampling Frequency** [2] |
| --- | --- | --- | --- |
| **Major Dischargers (see Tables 1A and 1B)** | | | |
| Mercury, Total [3],[8] | µg/L | C-24 or Grab [5] | 1/Month |
| PCBs, Total (as Aroclors) [6] | µg/L | C-24 | 2/Year |
| PCBs (as congeners) [7] | µg/L | C-24 | 1/Quarter  (for design flow [8] > 5.0 MGD) |
| 2/Year  (if design flow [8] ≤ 5.0 MGD) |
| **Minor Dischargers (see Tables 1A and 1B)** | | | |
| Mercury, Total [4] | µg/L | C-24 or Grab [5] | 1/Quarter |
| PCBs, Total (as Aroclors) [6] | µg/L | C-24 | 1/Year |
| PCBs (as congeners) [7],[9] | µg/L | C-24 | 1/Year |

Unit Abbreviations:

µg/L = micrograms per liter

MGD = million gallons per day

Sampling Types and Frequencies:

C-24 = 24-hour Composite

Grab = grab sample

1/Month = once per month

1/Quarter = once per quarter

2/Year = twice per year

1/Year = once per year

Footnotes:

[1] 24-hour composites may be made up of discrete grab samples collected over a 24-hour period, or may be collected using automatic compositing equipment. If using compositing equipment, the Discharger shall implement all feasible ultra clean techniques to reduce sample contamination (such as using ultra clean Teflon tubing).

[2] Intermittent or seasonal Dischargers shall collect samples during those months for which a discharge occurs.

[3] The Dischargers shall use ultra-clean sampling (U.S. EPA Method 1669) and ultra-clean analytical methods (U.S. EPA Method 1631) for total mercury monitoring.

[4] If allowed in the Pretreatment and Biosolids Monitoring Requirements of the Dischargers’ individual NPDES permits, grab samples may be collected coincident with composite samples collected for the analysis of other regulated parameters.

[5] Dischargers shall use U.S. EPA Method 608 for Aroclor monitoring. These data will be used for assessing compliance with the limits in Tables 4B and 5B. Non-detected and/or estimated values shall be treated as zeros in the calculation of Total PCBs.

[6] PCBs congeners monitoring is for informational purposes. Dischargers shall use U.S. EPA Proposed Method 1668C and report the results for each of the 40 congeners that contribute to the Bay’s impairment and congeners that co-elute with the 40 congeners (see Table F-14). For congeners that co-elute with the 40 congeners, Dischargers shall report the sum of these co-eluting congeners. A summation for total PCBs is not required.

[7] The design flows for each facility are included in Tables F-1A and F-1B of the Fact Sheet.

[8] For Sanitary District No. 5 of Marin County (Paradise Cove) and Crockett Community Services District (Port Costa), the minimum monitoring frequency for total mercury shall be annually.

[9] For Sanitary District No. 5 of Marin County (Paradise Cove) and Crockett Community Services District (Port Costa), the minimum monitoring frequency for PCBs congeners shall be once in this Order’s effective term.

IV. Reporting Requirements

A. General Monitoring and Reporting Requirements

The Dischargers shall comply with all Standard Provisions (Attachments D and G in the Dischargers’ individual NPDES permits) related to monitoring, reporting, and recordkeeping. These attachments are included in the Dischargers’ individual permits.

1. Individual Reporting in Self-Monitoring Reports (SMRs)

1. SMR Format. Dischargers shall electronically submit SMRs using the State Water Board’s California Integrated Water Quality System (CIWQS) website (http://www.waterboards.ca.gov/water\_issues/programs/ciwqs). The CIWQS website will provide additional information for SMR submittal in the event of a planned service interruption for electronic submittal.

**2. Mercury and PCBs Data.**

**a.** **Routine SMRs —** Dischargers shall submit mercury and PCBs data collected as part of this Order in the routine monthly or quarterly SMRs required in Dischargers’ individual NPDES permits. This includes data for mercury, total PCBs as Aroclors (using U.S. EPA Method 608), and PCBs as congeners (using U.S. EPA Method 1668C). The PCBs congeners shall include the 40 that contribute to water quality impairment plus co-elutes (59 to 66 congeners in total, see Tables F‑9 and F-10), using U.S. EPA Method 1668C.

* + - 1. **Discharge Adjustments.** For Industrial Dischargers claiming a discharge adjustment for recycled water use pursuant to Provision VI.C.5, the amount of adjustment claimed for that month shall be reported monthly to the Municipal Discharger that supplied the recycled water. The reporting from the Industrial Discharger to the Municipal Discharger shall be completed no later than 15 days following the end of the calendar month. The Municipal and Industrial Dischargers shall then include this information in their respective monthly (or quarterly) and annual SMRs.

Each SMR shall include all new mercury or PCBs monitoring results obtained since the last SMR was submitted. If a Discharger monitors mercury or PCBs more frequently than required by this Order, the Discharger shall include the results of such monitoring in the calculations and reporting for the SMR.

**b. Annual SMR —** Annual SMRs shall be due February 1 each year, covering the previous calendar year. The annual SMR shall contain a summary of its mercury data. This summary shall include, at a minimum, mercury concentrations for each sample, the corresponding flow, and the annual mercury loading.

**3. Specifications for Submitting SMRs to CIWQS.** Dischargers shall submit analytical mercury, total PCBs as Aroclors (using U.S. EPA Method 608), and PCBs as congeners (using U.S. EPA Method 1668C) results to CIWQS in electronic reporting format by EDF/CDF upload or through manual entry.

Dischargers shall arrange all reported data in a tabular format and summarize the data to clearly illustrate whether their Facility is operating in compliance with the effluent limitations. When electronic submittal of data is required and CIWQS does not provide for entry into a tabular format, the Discharger shall electronically submit the data in a tabular format as an attachment.

**4. Monitoring Periods.** Monitoring periods for all required monitoring shall be as set forth below unless otherwise specified:

Table E-4. Monitoring Periods

| **Sampling Frequency** | **Monitoring Period Begins On…** | **Monitoring Period** |
| --- | --- | --- |
| 1/Month | Order effective date | First day of calendar month through last day of calendar month |
| 1/Quarter | Closest January 1, April 1, July 1, October 1 before or after Order effective date [1] | January 1 through March 31  April 1 through June 30  July 1 through September 30 |
| 2/Year | Closest January 1 or July 1 before or after Order effective date [1] | January 1 through June 30  July 1 through December 31 |
| 1/Year | Closest January 1 before or after Order effective date [1] | January 1 through December 31 |
| Once | Order effective date | Once during Order term such that result is included with application for permit reissuance |

Footnote:

[1] Monitoring performed during the previous order term may be used to satisfy monitoring required by this Order.

**5. RL and MDL Reporting.** Dischargers shall report with each sample result the Reporting Level (RL) and Method Detection Limit (MDL) as determined by the procedure in 40 C.F.R. part 136. Dischargers shall report the results of analytical determinations for the presence of chemical constituents in a sample using the following reporting protocols:

**a.** Sample results greater than or equal to the RL shall be reported as measured by the laboratory (i.e., the measured chemical concentration in the sample).

**b.** Sample results less than the RL, but greater than or equal to the laboratory’s MDL, shall be reported as “Detected, but Not Quantified,” or DNQ. The estimated chemical concentration of the sample shall also be reported.   
  
For purposes of data collection, the laboratory shall write the estimated chemical concentration next to DNQ. The laboratory may, if such information is available, include numerical estimates of the data quality for the reported result. Numerical estimates of data quality may be percent accuracy (+/‑ a percentage of the reported value), numerical ranges (low to high), or any other means the laboratory considers appropriate.

**c.** Sample results less than the laboratory’s MDL shall be reported as “Not Detected”, or ND.

* 1. **PCBs Congeners Reporting.** General requirements for reporting U.S. EPA Method 1668C data are as follows:

**a. Minimum Levels —** The ML for each congener shall be published Method MLs (Table 2, EPA1668C). The laboratory analyzing the samples must have on file data demonstrating a lower calibration limit that is equal to or less than the published Method ML. Laboratories may revise the lower calibration limits based on final published values when U.S. EPA Method 1668C is fully approved or promulgated.

**b. Method Detection Limits —**The MDLs reported by the laboratory shall meet the criteria set in U.S. EPA Method 1668C. The laboratory shall demonstrate capability by achieving MDLs below method-specified MDLs. The MDL is based on analysis of low-level replicates of clean matrices (deionized water). Sample-specific detection limits (SSDLs) for each congener shall be reported when there is a ND result. The SSDL is calculated by using the instrument processing method based on the noise level in the vicinity of the largest peak in sample extracts containing the real matrix.

**c. Co-elution —** Congeners in a co-elution shall be reported as a combination of the congeners, with the lowest numerically designated congener reported first and separated by a slash (/) from numerically higher designated congeners.

For example, if PCB congeners 020, 021, and 033 are co-eluted, the Discharger shall report the co‑elution as PCB 020/021/033.

**d**. **Qualifiers —** Qualifiers allowed in reporting U.S. EPA 1668C data are as follows:

Table E-5. U.S. EPA Method 1668C Qualifiers in CIWQS

|  |  |  |
| --- | --- | --- |
| **Qualifiers** | **CIWQS Field** | **Qualifier Description** |
| ND | Qualifier | The analyte was not detected in the sample at the SSDL. |
| DNQ | Qualifier | The reported result is an estimate. The concentration is greater than the SSDL but is less than the method-specified ML. |
| M | QA Code | Estimated maximum possible concentration. |
| D | QA Code | Result obtained from the analysis of a dilution. |
| B | QA Code | Congener is present in the method blank. |

**e. Method Blank Correction —** Results shall be reported without method blank correction.

**f. Units** **—** Concentrations shall be reported in picograms per liter (pg/L).

* 1. **Transmittal Letter.** Each Discharger shall attach a transmittal letter to its SMR. The transmittal letter shall clearly identify violations of the WDRs set forth in this Order and any exceedances of trigger levels. The Discharger shall also describe the requirement that was violated or the trigger that was exceeded, discuss corrective actions taken or planned, and propose a time schedule for the corrective actions.

C. Discharge Monitoring Reports (DMRs)

DMRs are U.S. EPA reporting requirements. Dischargers shall electronically certify and submit DMRs together with SMRs using the Electronic Self-Monitoring Reports module eSMR 2.5 or the latest upgraded version. Electronic DMR submittal shall be in addition to electronic SMR submittal. Information about electronic DMR submittal is available at the DMR website at <http://www.waterboards.ca.gov/water_issues/programs/discharge_monitoring>.

1. FF

ATTACHMENT F - FACT SHEET

Contents

[I. Permit Information F-3](#_Toc487829684)

[II. Facility Description F-11](#_Toc487829685)

[A. Wastewater Treatment F-11](#_Toc487829686)

[B. Discharge Point and Receiving Waters F-12](#_Toc487829687)

[C. Previous Requirements F-12](#_Toc487829688)

[D. Compliance Summary F-12](#_Toc487829689)

[III. Applicable Plans, Policies, and Regulations F-14](#_Toc487829690)

[IV. Rationale For Effluent Limitations and Discharge Specifications F-16](#_Toc487829691)

[A. Water Quality-Based Effluent Limitations (WQBELs) F-17](#_Toc487829692)

[1. Scope and Authority F-17](#_Toc487829693)

[2. Beneficial Uses and Water Quality Criteria and Objectives F-17](#_Toc487829694)

[3. Need for WQBELs (Reasonable Potential Analysis) F-17](#_Toc487829695)

[4. WQBEL Calculations F-18](#_Toc487829696)

[D. Discharge Requirement Considerations F-26](#_Toc487829697)

[V. Rationale for Receiving Water Limitations F-27](#_Toc487829698)

[VI. Rationale for Provisions F-27](#_Toc487829699)

[A. Standard Provisions F-27](#_Toc487829700)

[B. Monitoring and Reporting F-27](#_Toc487829701)

[C. Special Provisions F-28](#_Toc487829702)

[1. Reopener Provisions F-28](#_Toc487829703)

[2. Triggers for Additional Mercury Control F-28](#_Toc487829704)

[3. Mercury and PCBs Source Control Program F-29](#_Toc487829705)

[4. Risk Reduction Programs F-30](#_Toc487829706)

[5. Mercury and PCBs Discharge Adjustments for Recycled Wastewater Use by Industrial Dischargers F-30](#_Toc487829707)

[6. PCBs Discharge Adjustment for Urban Stormwater Treatment by Municipal Dischargers F-31](#_Toc487829712)

[VII. Rationale for Monitoring and Reporting Program (MRP) F-31](#_Toc487829716)

[VIII. Public Participation F-32](#_Toc487829717)

Tables

[Table F-1A. Municipal Facility Information F-3](#_Toc487829731)

[Table F-1B. Industrial Facility Information F-6](#_Toc487829732)

[Table F-2A. Additional Municipal Facility Information F-7](#_Toc487829733)

[Table F-2B. Additional Industrial Facility Information F-10](#_Toc487829734)

[Table F-3. Beneficial Uses F-15](#_Toc487829735)

[Table F-4. Mass Emission Allocations for Municipal Dischargers F-18](#_Toc487829736)

[Table F-5. Mass Emission Allocations for Industrial Dischargers F-19](#_Toc487829737)

[Table F-6. Concentration-based Effluent Limitations for Municipal Dischargers F-22](#_Toc487829738)

ATTACHMENT F – FACT SHEET

This Fact Sheet includes the legal requirements and technical rationale that serve as the basis for the requirements of this Order. As described in section II.B of the Order, the Regional Water Board incorporates this Fact Sheet as findings supporting the issuance of the Order.

I. Permit Information

The following table summarizes administrative information related to the Dischargers’ facilities:

Table F-1A. Municipal Facility Information

| **Discharger** | **Facility Contact, Title, and Phone** | **Mailing Address** | **Effluent Description** | **Facility Design Flow (MGD)** |
| --- | --- | --- | --- | --- |
| American Canyon, City of | Stacey Ambrose,  Environmental Services Manager  (707) 647-4542 | 151 Mezzetta Court  American Canyon, CA 94503  Napa County | Advanced Secondary | 2.5 |
| Benicia, City of | Jeff Gregory, Wastewater Treatment Plant Superintendent  (707) 746-4790 | 614 East Fifth Street  Benicia, CA 94510  Solano County | Secondary | 4.5 |
| Burlingame, City of | Manuel Molina,  Project Manager  (650) 342-3727 | 501 Primrose Burlingame, CA 94010  San Mateo County | Secondary | 5.5 |
| Calistoga, City of | Mike Kirn  Public Works Director  (707) 942-2828 | 414 Washington Street Calistoga, CA 94515  Napa County | Secondary | 0.84 |
| Central Contra Costa Sanitary District | Ann K. Sasaki  Deputy General Manager  (925) 228-9500 | 5019 Imhoff Place  Martinez, CA 94553  Contra Costa County | Secondary | 53.8 |
| Central Marin Sanitation Agency | Jason Dow, General Manager  (415) 459-1455 | 1301 Andersen Drive  San Rafael, CA 94901  Marin County | Secondary | 10 |
| Crockett Community Services District, Port Costa Sanitary Department | James Barnhill,  Sanitary Department Manager  (510) 787-2992 | P.O. Box 578  Crockett, CA 94525  Contra Costa County | Secondary | 0.033 |
| Delta Diablo Sanitation District | Gary W. Darling, General Manager  (925) 756-1920 | 2500 Pittsburg-Antioch Highway Antioch, CA 94509  Contra Costa County | Secondary | 19.5 |
| East Bay Dischargers Authority | Michael S. Connor, General Manager (510) 278-5910 | 2651 Grant Avenue San Lorenzo, CA 94580  Alameda County | Secondary | 107.8 |
| City of Hayward |
| City of San Leandro |
| Oro Loma and Castro Valley Sanitary Districts |
| Union Sanitary District |
| Livermore-Amador Valley Water Management Agency |
| Dublin San Ramon Services District |
| City of Livermore |
| East Bay Municipal Utility District | Chris Dembiczak, Senior Environmental Health & Safety Specialist  (510) 287-0509 | P.O. Box 24055 Oakland, CA  94623-1055  Alameda County | Secondary | 120 |
| Fairfield-Suisun Sewer District | Gregory G. Baatrup,  General Manager  (707) 428-9162 | 1010 Chadbourne Road  Fairfield, CA 94534  Solano County | Advanced Secondary | 17.5 |
| Las Gallinas Valley Sanitary District | Mark Williams,  District Manager  (415) 472-1734 | 300 Smith Ranch Road  San Rafael, CA 94903  Marin County | Secondary | 2.92 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | Tony Rubio  Chief Plant Operator  (415) 435-1501 | P.O. Box 227  Tiburon, CA 94920  Marin County | Secondary | 0.04 |
| Marin County (Tiburon), Sanitary District No. 5 of | Tony Rubio  Chief Plant Operator  (415) 435-1501 | 2001 Paradise Drive Tiburon, CA 94920  Marin County | Secondary | 0.98 |
| Millbrae, City of | Daniel Mount,  Superintendent  (650) 259-2388 | 621 Magnolia Avenue Millbrae, CA 94030  San Mateo County | Secondary | 3.0 |
| Mt. View Sanitary District | Neal Allen,  District Manager  (925) 228-5635 ext. 32 | P. O. Box 2757 Martinez, CA 94553  Contra Costa County | Advanced Secondary | 3.2 |
| Napa Sanitation District | Tim Healy,  General Manager  (707) 258-6000 | P.O. Box 2480  Napa, CA 94558  Napa County | Secondary | 15.4 |
| Novato Sanitary District | Sandeep Karkal,  Manager-Engineer  (415-892-1694 | 500 Davidson Street  Novato, CA 94945  Marin County | Secondary | 7.0 |
| Palo Alto, City of | James Allen,  Plant Manager  (650) 329-2243 | 2501 Embarcadero Way,  Palo Alto, CA 94303  Santa Clara County | Advanced Secondary | 39 |
| Petaluma, City of | Matthew Pierce,  Operations Supervisor  (707) 776-3777 | 202 N. McDowell Blvd.  Petaluma, CA 94954  Sonoma County | Secondary | 6.7 |
| Pinole, City of | Ron Tobey,  Plant Manager  (510) 724-8963 | 2131 Pear Street, Pinole, CA 94564  Contra Costa County | Secondary | 4.06 |
| Rodeo Sanitary District | Steven S. Beall,  District Manager  (510) 799-2970 | 800 San Pablo Avenue  Rodeo, CA 94572  Contra Costa County | Secondary | 1.14 |
| Saint Helena, City of | Steven Palmer,  Public Works Director  (707) 967-2792 | 1480 Main Street  St. Helena, CA 94574  Napa County | Secondary | 0.5 |
| San Francisco (San Francisco International Airport), City and County of | Peter Acton,  Director of Facilities  (650) 821-5400 | P.O. Box 8097  San Francisco, CA 94128  San Mateo County | Secondary | 2.2 |
| San Francisco (Southeast Plant), City and County of | Mark A. Harris,  Operations Superintendent  (415) 920-4923 | 1155 Market St.,  11th Floor  San Francisco, CA 94103  San Francisco County | Secondary | 85.4 |
| San Jose and Santa Clara, Cities of | James Ervin,  Environmental Compliance Officer  (408) 945-5124 | 700 Los Esteros Road San Jose, CA 95134  Santa Clara County | Advanced Secondary | 167 |
| San Mateo, City of | Jan Guy,  Chief Plant Operator  (650) 522-7386 | 330 West 20th Avenue  San Mateo, CA 94403 | Secondary | 15.7 |
| Sausalito-Marin City Sanitary District | Omar Arias-Montez,  General Manager  (415) 331-4716 | 1 East Road  Sausalito, CA 94965  Marin County | Secondary | 1.8 |
| Sewerage Agency of Southern Marin | Mark Grushayev,  General Manager  (415) 384-4825 | 26 Corte Madera Ave. Mill Valley, CA 94941  Marin County | Secondary | 3.6 |
| Silicon Valley Clean Water | Daniel Child,  General Manager  (650) 591-7121 | 1400 Radio Road  Redwood City, CA 94065  San Mateo County | Secondary | 29 |
| Sonoma Valley County Sanitation District | Pam Jeane,  Assistant General Manager  (707) 521-1864 | Sonoma County Water Agency  404 Aviation Blvd.  Santa Rosa, CA 95403 | Secondary | 3.0 |
| South San Francisco and San Bruno, Cities of | Brian Schumacker,  Plant Superintendent  (650) 877-8555 | 195 Belle Air Road  South San Francisco, CA 94080  San Mateo County | Secondary | 13 |
| Sunnyvale, City of | Bhavani Yerrapotu  WPCP Division Manager  (408) 730-7268 | Sunnyvale Water Pollution Control Plant P.O. Box 3707 Sunnyvale, CA  94088-3707 | Advanced Secondary | 29.5 |
| U.S. Department of Navy (Treasure Island) | Patricia A. McFadden  Base Operations Manager  San Francisco Bay Area  (415) 743-4720 | 1 Avenue of the Palms, Suite 161  San Francisco, CA  94130  San Francisco County | Secondary | 2.0 |
| Vallejo Sanitation and Flood Control District | Melissa Morton  District Manager  (707) 644-8949 | 450 Ryder Street  Vallejo, CA 94590  Solano County | Secondary | 15.5 |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | Brian E. Hill,  Water Quality Manager  510-237-6693 | 2910 Hilltop Drive  Richmond, CA  94806  Contra Costa County | Secondary | 28.5 |
| Yountville, Town of | Donald Moore  Wastewater System Supervisor  (707) 944-2988 | 6550 Yount Street  Yountville, CA 94599  Napa County | Secondary | 0.55 |

Table F-1B. Industrial Facility Information

| **Discharger** | **Facility Contact, Title, and Phone** | **Mailing Address** | **Type of Facility** | **Facility Design Flow (MGD)** |
| --- | --- | --- | --- | --- |
| **Industrial Wastewater Discharger (Non-Petroleum Refinery):** | | | | |
| C&H Sugar Company, Inc., and Crockett Community Services District, Crockett Sanitary Department | C&H Sugar Company  Tanya Akkerman,  Environmental Compliance Manager (510) 787-4352  Crockett Sanitary Dept.  Dale McDonald,  General Manager  (510) 787-2992 | C&H Sugar Company  830 Loring Avenue  Crockett, CA 94525  Contra Costa County  Crockett Sanitary Dept.  P.O. Box 578  Crockett, CA 94525  Contra Costa County | Sugar Cane Crystalline Industry | 1.8 |
| Crockett Cogeneration, LP | Christopher Sargent,  Environmental Coordinator  (510) 787-4101 | 550 Loring Avenue  Crockett, CA 94525-1232  Contra Costa County | Industrial – Electrical Generation, SIC Code 4931 | 0.5 |
| Eco Services Operations LLC | Anthony Koo,  Senior Environmental Engineer  (925) 313-8221 | 100 Mococo Road  Martinez, CA 94553  Contra Costa County | Industrial – Chemical and Allied Products, SIC Code 2891 | 0.8 |
| GenOn Delta, LLC | Lawrence J. Penn,  Plant Operator  (925) 427-3583 | P.O. Box 192  Pittsburg, CA 94565  Contra Costa County | Electric Power generation | 2.2 |
| USS-Posco Industries | Freddy Ripoli,  Environmental Health & Safety Group Manager  (925) 439-6316 | 900 Loveridge Road  Pittsburg, CA 94565  Contra Costa County | Industrial - SIC Code 3312 | 28 |
| **Industrial Wastewater Discharger (Petroleum Refinery):** | | | | |
| Chevron Products Company | Kory Judd,  General Manager  (510) 242-4400 | 841 Chevron Way  Richmond, CA 94801  Contra Costa County | Industrial - Petroleum Refining | 25 |
| Phillips 66 | Donald R. Landeck,  Environmental Engineer  (510) 245-4618 | 1380 San Pablo Avenue  Rodeo, CA 94572-1354  Contra Costa County | Industrial – Petroleum Refining | 10 |
| Shell Oil Products US and Equilon Enterprises LLC | Thomas Rizzo,  General Manager  (925) 313-3000 | 3485 Pacheco Blvd  Martinez CA 94553  Contra Costa County | Industrial – Petroleum Refining | 8.2 |
| Tesoro Refining & Marketing Co. | Peter Carroll,  Environmental Engineer  (925) 335-3497 | 150 Solano Way  Martinez, CA 94553  Contra Costa County | Industrial - Petroleum Refining | 10.4 |
| Valero Refining Company | Kimberly Ronan,  Environmental Engineer  (707) 745-7990 | 3400 East Second Street  Benicia, CA 94510-1005  Solano County | Industrial - Petroleum Refining | 3.7 |

Table F-2A. Additional Municipal Facility Information

| **Discharger** | **Authorized Person to Sign and Submit Reports** | **Billing Address** | **Pretreatment Program** | **Receiving Water Type** |
| --- | --- | --- | --- | --- |
| American Canyon, City of | Stacey Ambrose,  Environmental Services Manager  (707) 647-4542 | 151 Mezzetta Court  American Canyon, CA 94503  Napa County | Yes | Estuarine |
| Benicia, City of | Jeff Gregory, Wastewater Treatment Plant Superintendent  (707) 746-4790 | 614 East Fifth Street  Benicia, CA 94510  Solano County | Yes | Estuarine |
| Burlingame, City of | Manuel Molina,  Project Manager  (650) 342-3727 | 501 Primrose Burlingame, CA 94010  San Mateo County | Yes | Marine |
| Calistoga, City of | Mike Kirn  Public Works Director  (707) 942-2828 | 414 Washington Street Calistoga, CA 94515  Napa County | No | Freshwater |
| Central Contra Costa Sanitary District | Ann K. Sasaki  Deputy General Manager  (925) 228-9500 | 5019 Imhoff Place  Martinez, CA 94553  Contra Costa County | Yes | Estuarine |
| Central Marin Sanitation Agency | Jason Dow, General Manager  (415) 459-1455 | 1301 Andersen Drive  San Rafael, CA 94901  Marin County | Yes | Estuarine |
| Crockett Community Services District, Port Costa Sanitary Department | James Barnhill,  Sanitary Department Manager  (510) 787-2992 | P.O. Box 578  Crockett, CA 94525  Contra Costa County | No | Estuarine |
| Delta Diablo Sanitation District | Gary W. Darling, General Manager  (925) 756-1920 | 2500 Pittsburg-Antioch Highway Antioch, CA 94509  Contra Costa County | Yes | Estuarine |
| East Bay Dischargers Authority | Michael S. Connor, General Manager (510) 278-5910 | 2651 Grant Avenue San Lorenzo, CA 94580  Alameda County | Yes | Estuarine |
| City of Hayward |
| City of San Leandro |
| Oro Loma and Castro Valley Sanitary Districts |
| Union Sanitary District |
| Livermore-Amador Valley Water Management Agency |
| Dublin San Ramon Services District |
| City of Livermore |
| East Bay Municipal Utility District | Eileen White, Director of Wastewater  (510) 287-1149 | P.O. Box 24055, MS#59 Oakland, CA  94623-1055  Alameda County | Yes | Marine |
| Fairfield-Suisun Sewer District | Brian Hawley,  Operations Manager  (707) 428-9118 | 1010 Chadbourne Road  Fairfield, CA 94534  Solano County | Yes | Estuarine |
| Las Gallinas Valley Sanitary District | Mark Williams,  District Manager  (415) 472-1734 | 300 Smith Ranch Road  San Rafael, CA 94903  Marin County | No | Estuarine |
| Marin County (Paradise Cove), Sanitary District No. 5 of | Tony Rubio  Chief Plant Operator  (415) 435-1501 | P.O. Box 227  Tiburon, CA 94920  Marin County | No | Marine |
| Marin County (Tiburon), Sanitary District No. 5 of | Tony Rubio  Chief Plant Operator  (415) 435-1501 | 2001 Paradise Drive Tiburon, CA 94920  Marin County | No | Marine |
| Millbrae, City of | Daniel Mount,  Superintendent  (650) 259-2388 | 621 Magnolia Avenue Millbrae, CA 94030  San Mateo County | No | Marine |
| Mt. View Sanitary District | Neal Allen,  District Manager  (925) 228-5635 ext. 32 | P. O. Box 2757 Martinez, CA 94553  Contra Costa County | No | Estuarine |
| Napa Sanitation District | Tim Healy,  General Manager  (707) 258-6000 | P.O. Box 2480  Napa, CA 94558  Napa County | Yes | Estuarine |
| Novato Sanitary District | Sandeep Karkal,  Manager-Engineer  (415-892-1694 | 500 Davidson Street  Novato, CA 94945  Marin County | Yes | Estuarine |
| Palo Alto, City of | James Allen,  Plant Manager  (650) 329-2243 | 2501 Embarcadero Way,  Palo Alto, CA 94303  Santa Clara County | Yes | Estuarine |
| Petaluma, City of | Matthew Pierce,  Operations Supervisor  (707) 776-3777 | 202 N. McDowell Blvd.  Petaluma, CA 94954  Sonoma County | Yes | Estuarine |
| Pinole, City of | Ron Tobey,  Plant Manager  (510) 724-8963 | 2131 Pear Street, Pinole, CA 94564  Contra Costa County | No | Marine |
| Rodeo Sanitary District | Steven S. Beall,  District Manager  (510) 799-2970 | 800 San Pablo Avenue  Rodeo, CA 94572  Contra Costa County | No | Estuarine |
| Saint Helena, City of | Steven Palmer,  Public Works Director  (707) 967-2792 | 1480 Main Street  St. Helena, CA 94574  Napa County | No | Freshwater |
| San Francisco (San Francisco International Airport), City and County of | Peter Acton,  Director of Facilities  (650) 821-5400 | P.O. Box 8097  San Francisco, CA 94128  San Mateo County | Yes | Marine |
| San Francisco (Southeast Plant), City and County of | Mark A. Harris,  Operations Superintendent  (415) 920-4923 | 1155 Market St.,  11th Floor  San Francisco, CA 94103  San Francisco County | Yes | Marine |
| San Jose and Santa Clara, Cities of | Kerry Romanow,  Director of Environmental Services  (408) 535-8550 | 700 Los Esteros Road San Jose, CA 95134  Santa Clara County | Yes | Estuarine |
| San Mateo, City of | Jan Guy,  Chief Plant Operator  (650) 522-7386 | 330 West 20th Avenue  San Mateo, CA 94403 | Yes | Marine |
| Sausalito-Marin City Sanitary District | Omar Arias-Montez,  General Manager  (415) 331-4716 | 1 East Road  Sausalito, CA 94965  Marin County | No | Marine |
| Sewerage Agency of Southern Marin | Mark Grushayev,  General Manager  (415) 384-4825 | 26 Corte Madera Ave. Mill Valley, CA 94941  Marin County | No | Marine |
| Silicon Valley Clean Water | Daniel Child,  General Manager  (650) 591-7121 | 1400 Radio Road  Redwood City, CA 94065  San Mateo County | Yes | Marine |
| Sonoma Valley County Sanitation District | Ryan Kirchner,  Operations Coordinator  (707) 495-6160 | Sonoma County Water Agency  404 Aviation Blvd.  Santa Rosa, CA 95403 | No | Estuarine |
| South San Francisco and San Bruno, Cities of | Brian Schumacker,  Plant Superintendent  (650) 877-8555 | 195 Belle Air Road  South San Francisco, CA 94080  San Mateo County | Yes | Marine |
| Sunnyvale, City of | Bhavani Yerrapotu  WPCP Division Manager  (408) 730-7268 | Sunnyvale Water Pollution Control Plant P.O. Box 3707 Sunnyvale, CA  94088-3707 | Yes | Estuarine |
| U.S. Department of Navy (Treasure Island) | Patricia A. McFadden  Base Operations Manager  San Francisco Bay Area  (415) 743-4720 | 1 Avenue of the Palms, Suite 161  San Francisco, CA  94130  San Francisco County | No | Marine |
| Vallejo Sanitation and Flood Control District | Melissa Morton  District Manager  (707) 644-8949 | 450 Ryder Street  Vallejo, CA 94590  Solano County | Yes | Estuarine |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | Brian E. Hill,  Water Quality Manager  510-237-6693 | 2910 Hilltop Drive  Richmond, CA  94806  Contra Costa County | Yes | Estuarine |
| Yountville, Town of | Donald Moore  Wastewater System Supervisor  (707) 944-2988 | 6550 Yount Street  Yountville, CA 94599  Napa County | No | Freshwater |

Table F-2B. Additional Industrial Facility Information

| **Discharger** | **Authorized Person to Sign and Submit Reports** | **Billing Address** | **Pretreatment Program** | **Receiving Water Type** |
| --- | --- | --- | --- | --- |
| **Industrial Wastewater Discharger (Non-Petroleum Refinery):** | | | | |
| C&H Sugar Company, Inc., and Crockett Community Services District, Crockett Sanitary Department | C&H Sugar Company  Tanya Akkerman,  Environmental Compliance Manager (510) 787-4352  Crockett Sanitary Dept.  Dale McDonald,  General Manager  (510) 787-2992 | C&H Sugar Company  830 Loring Avenue  Crockett, CA 94525  Contra Costa County  Crockett Sanitary Dept.  P.O. Box 578  Crockett, CA 94525  Contra Costa County | No | Estuarine |
| Crockett Cogeneration, LP | Dan Consie,  Vice President, Western Region  Consolidated Asset Management Services (CAMS)  (661) 387-7816 | 550 Loring Avenue  Crockett, CA 94525-1232  Contra Costa County | No | Estuarine |
| Eco Services Operations LLC | Anthony Koo,  Senior Environmental Engineer  (925) 313-8221 | 100 Mococo Road  Martinez, CA 94553  Contra Costa County | No | Estuarine |
| GenOn Delta, LLC | Lawrence J. Penn,  Plant Operator  (925) 427-3583 | P.O. Box 192  Pittsburg, CA 94565  Contra Costa County | No | Estuarine |
| USS-Posco Industries | Freddy Ripoli,  Environmental Health & Safety Group Manager  (925) 439-6316 | 900 Loveridge Road  Pittsburg, CA 94565  Contra Costa County | No | Estuarine |
| **Industrial Wastewater Discharger (Petroleum Refinery):** | | | | |
| Chevron Products Company | Kory Judd,  General Manager  (510) 242-4400 | 841 Chevron Way  Richmond, CA 94801  Contra Costa County | No | Marine |
| Phillips 66 | Mark E. Evans,  Refinery Manager  (510) 245-4415 | 1380 San Pablo Avenue  Rodeo, CA 94572-1354  Contra Costa County | No | Estuarine |
| Shell Oil Products US and Equilon Enterprises LLC | Gordon M. Johnson,  Manager of Environmental Affairs  (925) 313-3705 | 3485 Pacheco Blvd  Martinez CA 94553  Contra Costa County | No | Estuarine |
| Tesoro Refining & Marketing Co. | Matthew Buell,  Environmental Manager  (925) 370-3275 | 150 Solano Way  Martinez, CA 94553  Contra Costa County | No | Estuarine |
| Valero Refining Company | Donald W. Cuffel,  Director of Health, Safety, Environmental, and Governmental Affairs  (707) 745-7545 | 3400 East Second Street  Benicia, CA 94510-1005  Solano County | No | Estuarine |

**A.** Municipal Dischargers listed in Table 1A and Industrial Dischargers listed in Table 1B (collectively, Dischargers) own and operate their respective wastewater treatment plants and collection systems (collectively, Facilities). Municipal Facilities provide secondary or advanced secondary treatment of wastewater collected from their service areas, and Industrial Dischargers provide various levels of wastewater treatment depending on their activities. After treatment, both Municipal and Industrial Dischargers discharge to San Francisco Bay and its tributaries. Details of the Municipal and Industrial wastewater treatment processes and discharges are described in the individual NPDES permits listed in Attachment B of this Order.

For the purposes of this Order, references to “discharger” or “permittee” in applicable federal and State laws, regulations, plans, or policies are held to be equivalent to references to the Dischargers herein.

**B.** The Dischargers are regulated pursuant to NPDES Permit No. CA0038849. The Dischargers were previously subject to Order No. R2-2012-0096 (previous order). Order No. R2-2016-0008 amended Order No. R-2012-0096 to provide for an alternative monitoring program and remains in effect with this Order.  
The Dischargers are authorized to discharge subject to WDRs in this Order at the discharge locations described in Tables 2A and 2B of this Order. Regulations at 40 C.F.R. section 122.46 limit the duration of NPDES permits to a fixed term not to exceed five years. Accordingly, Table 3 of this Order limits the effective period for the discharge authorization. Pursuant to California Code of Regulations, title 23, section 2235.4, the terms and conditions of an expired permit are automatically continued pending reissuance of the permit if the Dischargers comply with all requirements for continuation of expired permits. (40 C.F.R § 122.6[d].)

**C.** This Order continues to implement the wasteload allocations and implementation requirements of the Mercury TMDL (adopted August 9, 2006) and PCBs TMDL (adopted February 13, 2008).

**D.** When applicable, State law requires dischargers to file a petition with the State Water Resources Control Board (State Water Board), Division of Water Rights, and receive approval for any change in the point of discharge, place of use, or purpose of use of treated wastewater that decreases the flow in any portion of a watercourse. The State Water Board retains separate jurisdictional authority to enforce such requirements under Water Code 1211. This is not an NPDES permit requirement.

II. Facility Description

A. Wastewater Treatment

1. **Locations and Service Areas**. The Municipal wastewater treatment plants are located throughout and the entire San Francisco Bay region. The Industrial wastewater treatment plants are located around San Pablo Bay, Carquinez Strait, and Suisun Bay.
2. **Wastewater Treatment.** Municipal wastewater treatment plants provide secondary treatment, which includes screening, skimming, settling, and biological treatment. Some plants also provide advanced secondary treatment, which removes additional solids often with sand filtration. Removing additional solids removes additional pollutants, including mercury and PCBs that adhere to particles. Municipal wastewater treatment plants generally remove over 90 percent of the mercury and PCBs in their influent. While the removed mercury and PCBs are not directly discharged to water, some is returned to the environment through landfills, incinerators, or soil amendments. The primary sources of mercury in municipal wastewater are expected to be human waste and medical and dental facilities.

Industrial Dischargers include petroleum refineries, chemical plants, and other large industrial facilities. Their mercury and PCBs loads depend on the types of activities in which they engage. The primary sources of PCBs are expected to be human waste and wastewater generated from old industrial equipment that may contain PCBs.

B. Discharge Point and Receiving Waters



The Municipal wastewater treatment plants discharge all throughout San Francisco Bay, including Lower South Bay, South Bay, Central Bay, San Pablo Bay, Carquinez Strait, Suisun Bay, and connected tributaries. Most Industrial wastewater treatment plants discharge to San Pablo Bay, Carquinez Strait, and Suisun Bay. Tables 2A and 2B of this Order specify the discharge locations for each facility. Attachment C shows a map of these discharge locations.

C. Previous Requirements

The effluent limitations from the previous order term remain unchanged in this Order.

D. Compliance Summary

1. **Mercury.** Mercury loads for Municipal and Industrial Dischargers have been well below their mass allocations since the previous order became effective in 2013, and has been consistently low in the years prior to 2013, as shown in the charts below.





**a.** **Municipal Dischargers —** In 2015, the municipal load was 2.2 kg/year, the lowest loading yet recorded. In 2016, the municipal load was 2.9 kg/year, which is comparable to the performance throughout the previous order term. The average municipal load of the previous order term was 75 percent below the mass allocation of 11 kg/year.

In the last order term, the most significant exceedance of mercury effluent limitations occurred from the U.S. Department of Navy Treasure Island Wastewater Treatment Plant, which violated its average weekly effluent limitation three times and its average monthly effluent limitation twice between January and February 2013. The U.S. Department of Navy determined that mercury-contaminated sediment may be present at its treatment plant and cleaned out sediment from the potential onsite sources (e.g., sumps, junction box). There have been no exceedances of mercury limitations or triggers since March 2013.

**b.** **Industrial Dischargers —**In 2015, the industrial load was 0.29 kg/year, the lowest loading in the previous order term. In 2016, the industrial load was 0.31 kg/year, which is comparable to most of the performance throughout the previous order term. The average industrial load of the previous order term was 59 percent below the mass allocation of 1.0 kg/year.

In the last order term, the most significant exceedance of mercury effluent limitations occurred from the Shell Martinez Refinery, which violated its maximum daily and average monthly effluent limitations twice between January and February 2017. Shell Martinez Refinery reported the high mercury concentrations were caused from heavy rains that resulted in poor solids removal. Shell Martinez Refinery reseeded its biotreater with healthier material, increased the frequency of carbon change-outs of granular activated carbon units, and increased the rate of solids removal at one of its treatment ponds.

1. **PCBs.** PCBs loads for Municipal and Industrial Dischargers have been well below their mass allocations since the previous order became effective in 2012, as shown in the charts below.

**a.** **Municipal Dischargers —**In 2016, the municipal PCBs load was 0.72 kg/year, which is comparable to the performance throughout the previous order term. The increase in PCBs between 2013 and the remainder of the previous order term could be due to timing of the quarterly samples, analytical variability, or mobilization of solids with legacy PCBs from the collection system during cleaning. Three of the largest municipal dischargers accounted for about 70 percent of the increase between 2013 and 2014. The average municipal load of the previous order term was 64 percent below the mass allocation of 2.0 kg/year. All Municipal Dischargers remained compliant with their PCBs effluent limitations in the previous order term.

**b.** **Industrial Dischargers —** In 2016, the industrial PCBs load was 0.012 kg/year, which is comparable to the performance throughout the previous order term. The average industrial load of the previous order term was 58 percent below the mass allocation of 0.031 kg/year. All Industrial Dischargers remained compliant with their PCBs effluent limitations in the previous order term.

III. Applicable Plans, Policies, and Regulations

**A.** **Legal Authorities**

This Order serves as WDRs pursuant to California Water Code article 4, chapter 4, division 7 (commencing with § 13260) for discharges to waters of the State. This Order is also issued pursuant to Clean Water Act (CWA) section 402 and implementing regulations adopted by U.S. EPA, and Water Code chapter 5.5, division 7 (commencing with § 13370). It shall serve as an NPDES permit for point sources discharges of mercury and PCBs from the Dischargers’ facilities listed in Attachment B to surface waters.

**B.** **California Environmental Quality Act**

Under Water Code section 13389, this action to adopt an NPDES permit is exempt from the provisions of the California Environmental Quality Act (CEQA), Public Resources Code division 13, chapter 3 (commencing with § 21100).

**C. State and Federal Regulations, Policies, and Plans**

**1.** **Water Quality Control Plan.** The Regional Water Board adopted the *Water Quality Control Plan for the San Francisco Bay Basin* (Basin Plan), which designates beneficial uses, establishes water quality objectives (WQOs), and contains implementation programs and policies to achieve those objectives for all waters addressed through the plan. Requirements in this Order implement the Basin Plan. In addition, this Order implements State Water Board Resolution No. 88‑63, which establishes State policy that all waters, with certain exceptions, should be considered suitable or potentially suitable for municipal or domestic supply. Beneficial uses applicable to San Francisco Bay are as shown in Table F-3.

Table F-3. Beneficial Uses

| **Discharge Point** | **Receiving Water Name** | **Beneficial Uses** |
| --- | --- | --- |
| 001 | San Francisco Bay and its tributaries [1] | Agricultural Supply (AGR)  Cold Freshwater Habitat (COLD)  Ocean, Commercial, and Sport Fishing (COMM)  Estuarine Habitat (EST)  Industrial Service Supply (IND)  Marine Habitat (MAR)  Fish Migration (MIGR)  Municipal and Domestic Supply (MUN)  Navigation (NAV)  Industrial Process Supply (PROC)  Preservation of Rare and Endangered Species (RARE)  Water Contact Recreation (REC1)  Non-Contact Water Recreation (REC2)  Shellfish Harvesting (SHELL)  Fish Spawning (SPWN)  Warm Freshwater Habitat (WARM)  Wildlife Habitat (WILD) |

Footnote:

[1] Specific beneficial uses that apply to each Discharger are included in the individual NPDES permits listed in Attachment B of this Order.

The Regional Water Board adopted a Basin Plan Amendment on August 9, 2006, that established new water quality objectives for mercury in addition to the San Francisco Bay Mercury TMDL to attain the new objectives in San Francisco Bay and contiguous Bay segments. The Regional Water Board’s Executive Officer made corrections on May 23, 2007, and the State Water Board approved the Basin Plan Amendment (as corrected) and the water quality objectives on July 17, 2007. The U.S. EPA approved the new water quality objectives on February 12, 2008.

The Regional Water Board also adopted a Basin Plan Amendment on February 13, 2008, that established waste load allocations for PCBs in San Francisco Bay and contiguous Bay segments. The State Water Board approved the Basin Plan amendment on October 20, 2009. The U.S. EPA approved the amendment on March 29, 2010.

**2. Sediment Quality.** The State Water Board adopted the *Water Quality Control Plan for Enclosed Bays and Estuaries – Part 1, Sediment Quality* on September 16, 2008, and it became effective on August 25, 2009. This plan supersedes other narrative sediment quality objectives, and establishes new sediment quality objectives and related implementation provisions for specifically defined sediments in most bays and estuaries. This Order implements the sediment quality objectives of this plan.

**3. National Toxics Rule (NTR) and California Toxics Rule (CTR).** U.S. EPA adopted the NTR on December 22, 1992, and amended it on May 4, 1995, and November 9, 1999. About 40 criteria in the NTR apply in California. On May 18, 2000, U.S. EPA adopted the CTR. The CTR promulgated new toxics criteria for California and incorporated the previously adopted NTR criteria that applied in the State. U.S. EPA amended the CTR on February 13, 2001. These rules contain federal water quality criteria for priority pollutants.

**4.** **State Implementation Policy.** On March 2, 2000, the State Water Board adopted the *Policy for Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries of California* (State Implementation Policy or SIP). The SIP became effective on April 28, 2000, with respect to the priority pollutant criteria U.S. EPA promulgated for California through the NTR and the priority pollutant objectives the Regional Water Board established in the Basin Plan. The SIP became effective on May 18, 2000, with respect to the priority pollutant criteria U.S. EPA promulgated through the CTR. The State Water Board adopted amendments to the SIP on February 24, 2005, that became effective on July 13, 2005. The SIP establishes implementation provisions for priority pollutant criteria and objectives, and provisions for chronic toxicity control. Requirements of this Order implement the SIP.

**5.** **Antidegradation Policy.** Federal regulations at 40 C.F.R. section 131.12 require that state water quality standards include an antidegradation policy consistent with the federal policy. The State Water Board established California’s antidegradation policy through State Water Board Resolution No. 68-16, *Statement of Policy with Respect to Maintaining High Quality of Waters in California,* which is deemed to incorporate the federal antidegradation policy where the federal policy applies under federal law. Resolution No. 68-16 requires that existing water quality be maintained unless degradation is justified based on specific findings. The Basin Plan implements, and incorporates by reference, both the State and federal antidegradation policies. Permitted discharges must be consistent with the antidegradation provisions of 40 C.F.R. section 131.12 and State Water Board Resolution No. 68-16. (See Fact Sheet section IV.D.2.)

**6.** **Anti-Backsliding Requirements.** CWA sections 402(o) and 303(d)(4) and 40 C.F.R. section 122.44(l) restrict backsliding in NPDES permits. These anti-backsliding provisions require that effluent limitations in a reissued permit be as stringent as those in the previous order, with some exceptions in which limitations may be relaxed. (See Fact Sheet section IV.D.1.)

**7.** **Endangered Species Act Requirements.** This Order does not authorize any act that results in the taking of a threatened or endangered species or any act that is now prohibited, or becomes prohibited in the future, under either the California Endangered Species Act (Fish and Game Code §§ 2050 to 2097) or the Federal Endangered Species Act (16 U.S.C.A. §§ 1531 to 1544). This Order requires compliance with effluent limits, receiving water limits, and other requirements to protect beneficial uses, including protecting rare, threatened, or endangered species. The Discharger is responsible for meeting all Endangered Species Act requirements.

**D. Impaired Waters on CWA 303(d) List**

In July 2015, U.S. EPA approved a revised list of impaired waters prepared pursuant to CWA section 303(d), which requires identification of specific water bodies where it is expected that water quality standards will not be met after implementation of technology-based effluent limitations on point sources. Where it has not done so already, the Regional Water Board plans to adopt TMDLs for pollutants on the 303(d) list. TMDLs establish wasteload allocations for point sources and load allocations for non-point sources, and are established to achieve the water quality standards for the impaired waters.

San Francisco Bay is listed as impaired by mercury and PCBs. On February 12, 2008, U.S. EPA approved a TMDL for mercury in San Francisco Bay. On March 29, 2010, U.S. EPA approved a TMDL for PCBs in San Francisco Bay. The Mercury and PCBs TMDLs apply to this discharge and are implemented through this Order (NPDES Permit No. CA0038849).

IV. Rationale For Effluent Limitations and Discharge Specifications

The CWA requires point source dischargers to control the amount of conventional, non‑conventional, and toxic pollutants discharged into waters of the United States. The control of pollutants discharged is established through effluent limitations and other requirements in NPDES permits. There are two principal bases for effluent limitations: 40 C.F.R. section 122.44(a) requires that permits include applicable technology-based limitations and standards; and 40 C.F.R. section 122.44(d) requires that permits include water quality-based effluent limitations to attain and maintain applicable numeric and narrative water quality criteria to protect the beneficial uses of receiving waters.

A. Water Quality-Based Effluent Limitations (WQBELs)

1. Scope and Authority

CWA section 301(b) and 40 C.F.R. section 122.44(d) require that permits include limitations more stringent than federal technology-based requirements where necessary to achieve applicable water quality standards. Water quality-based effluent limitations are included in this permit to implement wasteload allocations which are part of the San Francisco Bay Mercury and PCBs TMDLs.

2. Beneficial Uses and Water Quality Criteria and Objectives

Fact Sheet section III.C.1, above, identifies the beneficial uses of San Francisco Bay. Water quality criteria and objectives to protect these beneficial uses are described below:

1. **Mercury —** Basin Plan Table 3-3B specifies two mercury water quality objectives, which apply to all segments of San Francisco Bay, including all marine and estuarine waters contiguous to San Francisco Bay.
2. **Protection of Human Health.** The mercury water quality objective for protection of human health during fish consumption is 0.2 milligrams (mg) mercury per kilogram (kg) fish tissue (average wet weight concentration measured in the muscle tissue of fish large enough to be consumed by humans).
3. **Protection of Aquatic Organisms and Wildlife.** The mercury water quality objective for protection of aquatic organisms and wildlife is 0.3 mg mercury per kg fish (average wet weight concentration measured in whole fish 3 to 5 centimeters (cm) in length.
4. **PCBs —** Basin Plan section 7.2.3.1 includes a narrative water quality objective that states controllable water quality factors shall not cause a detrimental increase in toxic substances found in bottom sediments or aquatic life. The PCBs TMDL and implementation plan are designed to resolve PCB impairment in all segments of San Francisco Bay. For municipal and industrial wastewater discharges, this means limiting loads to 2.0 kg/year and 0.035 kg/year, respectively.

3. Need for WQBELs (Reasonable Potential Analysis)

The Regional Water Board is including WQBELs for mercury and PCBs in this Order that are consistent with the assumptions and requirements of the San Francisco Bay Mercury and PCBs TMDLs. Based on the water quality monitoring done at the time of these TMDL adoptions, which set the wasteload allocations for mercury and PCBs at levels necessary to attain water quality standards, the Regional Water Board has determined that the WQBELs are consistent with the assumptions of these TMDLs. Therefore, compliance with the effluent limitations will satisfy the requirements of the TMDL.

The Regional Water Board has developed WQBELs for mercury and PCBs pursuant to 40 C.F.R. section 122.44(d)(1)(vii), which does not require a reasonable potential analysis. Similarly, SIP section 1.3 recognizes that a reasonable potential analysis is not appropriate if a TMDL has been developed.

4. WQBEL Calculations

**a. Mercury —** This Order contains mass-based and concentration-based WQBELs:

1. **Mass-based WQBELs.** The mass-based WQBELs are based on the established aggregate wasteload allocations for Municipal Dischargers and Industrial Dischargers that comprise a portion of the San Francisco Bay Mercury TMDL. For the San Francisco Bay Mercury TMDL, loads are expressed in terms of annual mercury loads because the adverse effects of mercury occur through long-term bioaccumulation. The loads are intended to represent long-term averages and account for long-term variability, including seasonal variability.

Basin Plan Table 7.2.2-3 specifies the San Francisco Bay Mercury TMDL’s final aggregate mass emission limit and associated individual mass emission limits for Municipal Dischargers as shown in Table F-4 below.

Table F-4. Mass Emission Allocations for Municipal Dischargers

| **Discharger** | **NPDES Permit No.** | **Average Annual Effluent Limit for Mercury**  **(kg/yr)** |
| --- | --- | --- |
| American Canyon, City of | CA0038768 | 0.095 |
| Benicia, City of | CA0038091 | 0.088 |
| Burlingame, City of | CA0037788 | 0.089 |
| California Department of Parks and Recreation (Angel Island State Park) | - | 0013 |
| Calistoga, City of | CA0037966 | 0.016 |
| Central Contra Costa Sanitary District | CA0037648 | 1.3 |
| Central Marin Sanitation Agency | CA0038628 | 0.11 |
| Crockett Community Services District, Port Costa Sanitary Dept. | CA0037885 | 0.00072 |
| Delta Diablo Sanitation District | CA0038547 | 0.19 |
| East Bay Dischargers Authority | CA0037869 | 2.2 |
| Union S.D. Wet Weather Outfall | CA0038733 |
| Union S.D. Hayward Marsh | CA0038636 |
| Dublin San Ramon Services District | CA0037613 |
| City of Livermore | CA0038008 |
| LAVWMA Wet Weather Outfall | CA0038679 |
| East Bay Municipal Utility District | CA0037702 | 1.5 |
| Fairfield-Suisun Sewer District | CA0038024 | 0.17 |
| Las Gallinas Valley Sanitary District | CA0037851 | 0.10 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | CA0037427 | 0.00055 |
| Marin County (Tiburon), Sanitary District No. 5 of | CA0037753 | 0.0099 |
| Millbrae, City of | CA0037532 | 0.052 |
| Mt. View Sanitary District | CA0037770 | 0.034 |
| Napa Sanitation District | CA0037575 | 0.17 |
| Novato Sanitary District | CA0037958 | 0.079 |
| Palo Alto, City of | CA0037834 | 0.31 |
| Petaluma, City of | CA0037810 | 0.063 |
| Pinole, City of | CA0037796 | 0.055 |
| Rodeo Sanitary District | CA0037826 | 0.060 |
| Saint Helena, City of | CA0038016 | 0.047 |
| San Francisco (San Francisco International Airport), City and County of | CA0038318 | 0.032 |
| San Francisco (Southeast Plant), City and County of | CA0037664 | 1.6 |
| San Jose and Santa Clara, Cities of | CA0037842 | 0.8 |
| San Mateo, City of | CA0037541 | 0.19 |
| Sausalito-Marin City Sanitary District | CA0038067 | 0.078 |
| Sewerage Agency of Southern Marin | CA0037711 | 0.076 |
| Silicon Valley Clean Water | CA0038369 | 0.32 |
| Sonoma Valley County Sanitary District | CA0037800 | 0.041 |
| South San Francisco and San Bruno, Cities of | CA0038130 | 0.18 |
| Sunnyvale, City of | CA0037621 | 0.12 |
| U.S. Department of Navy, Treasure Island | CA0110116 | 0.026 |
| Vallejo Sanitation and Flood Control District | CA0037699 | 0.34 |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | CA0038539 | 0.23 |
| Yountville, Town of | CA0038121 | 0.040 |
| ***Total Aggregate Mass Emission Limit***[1] | - | ***11*** |

Unit Abbreviations:

kg/yr = kilograms per year

Footnote:

[1] Total differs slightly from the column sum due to rounding to the nearest kilogram.

Basin Plan Tables 7.2.2-4 and 7.2.2-5 specify the San Francisco Bay Mercury TMDL’s final aggregate mass emission limit and associated individual mass emission limits for Industrial Dischargers as shown in Table F-5 below.

Table F-5. Mass Emission Allocations for Industrial Dischargers

|  |  |  |
| --- | --- | --- |
| **Discharger** | **NPDES Permit No.** | **Average Annual Effluent Limit for Mercury**  **(kg/yr)** |
| **Industrial Dischargers (Non-Petroleum Refinery)** | | |
| C&H Sugar and Crockett Community Services District, Crockett Sanitary Dept. | CA0005240 | 0.045 |
| Crockett Cogeneration, LP, and Pacific Crockett Energy, Inc. | CA0029904 | 0.0047 |
| Dow Chemical Company | - | 0.041 |
| General Chemical | - | 0.21 |
| GWF Power Systems, Site I | - | 0.0016 |
| GWF Power Systems, Site V | - | 0.0025 |
| Hanson Aggregates, Amador Street | CA0030139 | 0.000005 |
| Hanson Aggregates, Tidewater Avenue, Oakland | CAA030147 | 0.000005 |
| Pacific Gas and Electric, East Shell Pond | - | 0.00063 |
| Pacific Gas and Electric, Hunters Point Power Plant | - | 0.020 |
| Eco Services Operations LLC | CA0006165 | 0.011 |
| GenOn Delta, LLC | CA0004880 | 0.0078 |
| San Francisco (San Francisco International Airport Industrial WWTP), City and County of | - | 0.051 |
| Southern Energy Delta LLC (Potrero Power Plant) | - | 0.0031 |
| U.S. Department of Navy (Point Molate) | - | 0.013 |
| USS-Posco Industries | CA0005002 | 0.045 |
| ***Total Aggregate Mass Emission Limit***[1] | - | ***0.4*** |
| **Industrial Dischargers (Petroleum Refinery)** | | |
| Chevron Products Company | CA0005134 | 0.34 |
| Phillips 66 | CA0005053 | 0.13 |
| Shell Oil Products US and Equilon Enterprises LLC | CA0005789 | 0.22 |
| Tesoro Refining & Marketing Co. | CA0004961 | 0.11 |
| Valero Refining Company | CA0005550 | 0.08 |
| ***Total Aggregate Mass Emission Limit***[1] | - | ***0.9*** |

Unit Abbreviations:

kg/yr = kilograms per year

Footnote:

[1] Total differs slightly from the column sum due to rounding.

[2] Wasteload allocations for industrial wastewater discharges do not include mass from once-through cooling water. The Regional Water Board will apply intake credits to once-through cooling water as allowed by law.

The waste load allocations are based on load estimates computed using available data on effluent mercury concentrations and effluent discharge volumes from 2000 through 2003. At the time of the San Francisco Bay Mercury TMDL development, the combined mercury load for all Municipal Dischargers discharging to San Francisco Bay and its tributaries was estimated to be about 17 kg/yr. The combined load for all Industrial Dischargers was estimated to be about 1.3 kg/yr. Together, these wastewater discharges were estimated to account for a load of about 18.3 kg/yr, or about two percent of the San Francisco Bay’s total mercury load.

The San Francisco Bay Mercury TMDL granted Municipal Dischargers a 20-year compliance schedule to ensure aggregate loads did not exceed a final limit of 11 kg/yr. However, the previous order imposed the final municipal limit of 11 kg/yr because municipal discharges had been well below this final limit. This early imposition of the final limit was pursuant to 40 C.F.R. section 122.47, which requires compliance as soon as possible.

This Order does not contain requirements for California Department of Parks and Recreation (Angel Island State Park) for municipal discharges and Dow Chemical Company, General Chemical, GWF Sites I and V, Hanson Aggregates (Olin Jones Dredge Spoils Disposal Facility), Pacific Gas and Electric, Southern Energy Delta LLC, and the U.S. Department of Navy (Point Molate) for industrial discharges because these dischargers have ceased discharging from their facilities, and the Regional Water Board has rescinded their NPDES permits. To account for these rescissions, this previous order reduced the aggregate industrial limit from 1.3 to 1.0 kg/yr. This Order retains the reduced aggregate industrial limit.

This Order also does not contain requirements for the Hanson Aggregates Amador Street and Tidewater Avenue facilities that are covered under NPDES Permit No. CAG982001, which covers aggregate mining, marine sand washing, and sand offloading activities and is consistent with the San Francisco Bay Mercury TMDL. In addition, this Order does not contain requirements for the San Francisco International Airport industrial wastewater treatment plant because it is regulated as a single site for both sanitary municipal and industrial activities. Because flows to the San Francisco International Airport’s treatment facility are now predominantly municipal, it is appropriate to regulate this facility as a municipal wastewater treatment plant. These facilities comprise a very small portion of the total wastewater mercury load to San Francisco Bay.

In 2016, the Regional Water Board adopted an individual NPDES permit (NPDES Permit No. CA0030228) for Schnitzer Steel Industries, Inc. This Order does not contain requirements for Schnitzer Steel Industries, Inc., because it discharges to the City of Oakland’s storm drain, which is covered under the Alameda County Clean Water Program wasteload allocation of 20 kg/yr and implemented through NPDES Permit No. CAS612008, which covers San Francisco Bay Mercury TMDL urban stormwater discharge requirements for regional stormwater discharges.

1. **Concentration-based WQBELs.** The concentration-based WQBELs are consistent with the San Francisco Bay Mercury TMDL and State Water Board’s Resolution No. 2007-0045 approving the TMDL, which states, in part, the following:

*…any NPDES permit or permits that implement the San Francisco Bay Mercury TMDL will include individual numeric effluent limitations consistent with the assumptions and requirements of waste load allocations for each wastewater discharger, that will be individually enforceable.*

A primary assumption and requirement of the San Francisco Bay Mercury TMDL is that wastewater dischargers maintain current treatment performance. This assumption is stated in the TMDL itself and its supporting documents, which state the following:

*The watershed NPDES permit for municipal facilities will put in place a set of triggered actions … intended … to ensure that municipal wastewater facilities maintain their ongoing operation, maintenance, and performance.” (p. 75, Staff Report for the TMDL, September 2, 2004)*

*[The TMDL’s] conditions are intended … to ensure that industrial wastewater facilities maintain proper operation, maintenance, and performance.” (BPA-20, Basin Plan Amendment, August 9, 2006)*

This Order retains the individual concentration-based limitations from the previous order, which are consistent with Municipal and Industrial Discharger’s performance levels, because Dischargers continue to perform be well below their mass allocation. Three separate performance categories were derived using mercury data between 2000 and 2003: municipal secondary treatment, municipal advanced secondary treatment, and industrial treatment performance. The data used to derive these performance-based limitations are from the same dataset used to calculate the San Francisco Bay Mercury TMDL’s initial wasteload allocations. Therefore, these performance-based limitations are consistent with attaining TMDL. Appendix F-2 of this Fact Sheet describe the effluent limitation calculations.

Non-petroleum refinery performance-based limitations were determined using performance data from petroleum refineries. This is because the performance-based trigger levels for all Industrial Dischargers in the TMDL were set using petroleum refinery data.

40 C.F.R. section 122.45(d) requires average monthly and average weekly effluent limitations for Municipal Dischargers and average monthly and maximum daily effluent limitations for Industrial Dischargers. These limitations are intended to minimize the potential for adverse effects in the immediate vicinity of discharges and to ensure that wastewater facilities maintain proper operation, maintenance, and performance. Individual concentration-based mercury effluent limitations for Municipal and Industrial Dischargers are shown in Tables F-6 and F-7 below.

Table F-6. Concentration-based Effluent Limitations for Municipal Dischargers

| **Discharger** | **Average Monthly Effluent Limit for Mercury(µg/L)** | **Average Weekly Effluent Limit for Mercury(µg/L** |
| --- | --- | --- |
| American Canyon, City of | 0.025 | 0.027 |
| Benicia, City of | 0.066 | 0.072 |
| Burlingame, City of | 0.066 | 0.072 |
| Calistoga, City of | 0.066 | 0.072 |
| Central Contra Costa Sanitary District | 0.066 | 0.072 |
| Central Marin Sanitation Agency | 0.066 | 0.072 |
| Crockett Community Services District, Port Costa Sanitary Dept. | 0.066 | 0.072 |
| Delta Diablo Sanitation District | 0.066 | 0.072 |
| East Bay Dischargers Authority | 0.066 | 0.072 |
| Union S.D. Wet Weather Outfall |
| Union S.D. Hayward Marsh |
| Dublin San Ramon Services District |
| City of Livermore |
| LAVWMA Wet Weather Outfall |
| East Bay Municipal Utility District | 0.066 | 0.072 |
| Fairfield-Suisun Sewer District | 0.025 | 0.027 |
| Las Gallinas Valley Sanitary District | 0.066 | 0.072 |
| Marin County (Paradise Cove), Sanitary District No. 5 of | 0.066 | 0.072 |
| Marin County (Tiburon), Sanitary District No. 5 of | 0.066 | 0.072 |
| Millbrae, City of | 0.066 | 0.072 |
| Mt. View Sanitary District | 0.025 | 0.027 |
| Napa Sanitation District | 0.066 | 0.072 |
| Novato Sanitary District | 0.066 | 0.072 |
| Palo Alto, City of | 0.025 | 0.027 |
| Petaluma, City of | 0.025 | 0.027 |
| Pinole, City of | 0.066 | 0.072 |
| Rodeo Sanitary District | 0.066 | 0.072 |
| Saint Helena, City of | 0.066 | 0.072 |
| San Francisco (San Francisco International Airport), City and County of | 0.066 | 0.072 |
| San Francisco (Southeast Plant), City and County of | 0.066 | 0.072 |
| San Jose and Santa Clara, Cities of | 0.025 | 0.027 |
| San Mateo, City of | 0.066 | 0.072 |
| Sausalito-Marin City Sanitary District | 0.066 | 0.072 |
| Sewerage Agency of Southern Marin | 0.066 | 0.072 |
| Silicon Valley Clean Water | 0.066 | 0.072 |
| Sonoma Valley County Sanitary District | 0.066 | 0.072 |
| South San Francisco and San Bruno, Cities of | 0.066 | 0.072 |
| Sunnyvale, City of | 0.025 | 0.027 |
| U.S. Department of Navy, Treasure Island | 0.066 | 0.072 |
| Vallejo Sanitation and Flood Control District | 0.066 | 0.072 |
| West County Agency; West County Wastewater District;  City of Richmond ; and Richmond Municipal Sewer District No. 1 | 0.066 | 0.072 |
| Yountville, Town of | 0.066 | 0.072 |

Unit Abbreviation:

µg/L = micrograms per liter

**Table F-7. Concentration-based Effluent Limitations for Industrial Dischargers**

|  |  |  |
| --- | --- | --- |
| **Discharger** | **Average Monthly Effluent Limit for Mercury (µg/L)** | **Maximum Daily Effluent Limit for Mercury (µg/L)** |
| **Industrial Dischargers (Non-Petroleum Refinery)** | | |
| C&H Sugar and Crockett Community Services District, Crockett Sanitary Department | 0.079 | 0.12 |
| Crockett Cogeneration, LP | 0.079 | 0.12 |
| Eco Services Operations LLC | 0.079 | 0.12 |
| GenOn Delta, LLC | 0.079 | 0.12 |
| USS-Posco Industries | 0.079 | 0.12 |
| **Industrial Dischargers (Petroleum Refinery)** | | |
| Chevron Products Company | 0.079 | 0.12 |
| Phillips 66 | 0.079 | 0.12 |
| Shell Oil Products US and Equilon Enterprises LLC | 0.079 | 0.12 |
| Tesoro Refining & Marketing Co. | 0.079 | 0.12 |
| Valero Refining Company | 0.079 | 0.12 |

Unit Abbreviation:

µg/L = micrograms per liter

**b. PCBs —** Basin Plan section 7.2.3.6 states that NPDES permits shall include performance‑based WQBELs that are consistent with the wasteload allocations of the San Francisco Bay PCBs TMDL. This Order retains the individual concentration-based effluent limitations from the previous order because these concentration limits resulted in mass discharges that complied with the TMDL (see Appendix F-3 for U.S. EPA 1668C data of 66 PCBs congeners used to calculate loads between 2013 and 2016).

Four separate performance categories were derived using PCBs data between 1999 and 2001 (included in Appendix F-4 of this Fact Sheet): municipal secondary treatment, municipal advanced secondary treatment, petroleum refinery, and non‑petroleum refinery. The data used to derive these performance‑based limitations are from the same dataset used to calculate the San Francisco Bay PCBs TMDL’s wasteload allocations. Therefore, these performance-based limitations are consistent with the TMDL. Calculating limits based on categories of treatment type reduce the likelihood of penalizing good performers and dischargers that have implemented effective control measures.

40 C.F.R. section 122.45(d) requires, unless impracticable, average monthly and average weekly effluent limitations for Municipal Dischargers and average monthly and maximum daily effluent limitations for Industrial Dischargers. This Order continues to implement a maximum daily effluent limitation instead of an average weekly effluent limitation for Municipal Dischargers, which is consistent with the U.S. EPA’s Technical Support Document. Technical Support Document section 5.2.3 states, “…in lieu of an AWL [average weekly effluent limitation] for POTWs, EPA recommends establishing an MDL [maximum daily effluent limitation] for toxic pollutants and pollutant parameters in water quality permitting.”

Consistent with previous orders, this Order does not establish mass-based limitations. Concentration-based limitations are more related to the performance of a facility because mass-based limitations rely on flows. Flows are highly influenced by rainfall, which is not within a Discharger’s control. Furthermore, the derivation of limitations with longer averaging periods, which would be required to establish mass-based limitations, requires frequent monitoring (e.g., monthly) in order to capture performance variability. Frequent monitoring is not a reasonable or practicable use of resources because the Municipal and Industrial Dischargers are a small source of PCBs to the San Francisco Bay (less than seven percent) relative to the high cost of PCBs analyses (approximately $1,000 each).

The performance-based limitations were derived from the 99 percent upper confidence limit (UCL) of the mean concentration for each dataset of the four performance categories. The 99 percent UCL was used on the mean of the datasets because of the high level of uncertainty in the actual mean (or actual performance) from the very small dataset for each discharge category used to establish TMDL allocations (the number of samples were between 6 and 14). The Regional Water Board then multiplied the resulting long‑term average for each performance category by the appropriate multiplier from the Technical Support Document to calculate the average monthly and maximum daily effluent limitations, as shown in Table F-8 below.

**Table F-8. PCBs WQBEL Calculations**

|  | **Secondary** | **Advanced Secondary** | **Petroleum Refinery** | **Non-Petroleum Refinery** |
| --- | --- | --- | --- | --- |
| **Units** | **µg/L** | **µg/L** | **µg/L** | **µg/L** |
| No. of data points <10 or at least 80% of data reported non detect? (Y/N) | Y | N | N | Y |
| Mean of TMDL effluent data points | 0.003556 | 0.00211 | 0.000272 | 0.003543 |
| Std Dev of TMDL effluent data points | 0.002206 | 0.000066 | 0.000199 | 0.001554 |
| Coefficient of Variation (CV), calculated | 0.62 | 0.31 | 0.73 | 0.44 |
| CV, Selected – Final | 0.60 | 0.31 | 0.73 | 0.60 |
| 99% UCL on the Mean = long term avg. | 0.005547 | 0.00025 | 0.000402 | 0.005678 |
| AMEL multiplier95 from U.S. EPA TSD | 2.13 | 1.58 | 2.37 | 2.13 |
| MDEL multiplier99 from U.S. EPA TSD | 3.11 | 1.94 | 3.70 | 3.11 |
| **AMEL** | **0.012** | **0.00039** | **0.00095** | **0.012** |
| **MDEL** | **0.017** | **0.00049** | **0.0015** | **0.018** |

These limitations are based on data for 40 congeners that are representative surrogates for the PCBs causing impairment. These 40 congeners are the same ones monitored in the Regional Monitoring Program (using U.S. EPA Method 1668A) that formed the basis for the impairment. As some other congeners co-elute with these 40 congeners (using U.S. EPA Method 1668C), the concentrations of as many as 66 congeners, if the laboratory uses a SB-Octyl column (shown in Table F-9 below), or as many as 59 congeners, if the laboratory uses a DB-1 column (shown in Table F-10 below), form the basis for the limits. Therefore, it would be reasonable and consistent with the San Francisco Bay PCBs TMDL (if U.S. EPA Proposed Method 1668C is an approved method at the time of the next permit reissuance) that any future compliance with effluent limitations be determined using the same congeners that were used in the derivation of the limits specified in this Order.

**Table F-9. PCB Congeners, Including Co-Elution (IUPAC No.)**

**with SB-Octyl Column for TMDL Development**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCB 005 | PCB 061 | PCB 099 | PCB 149 | PCB 181 |
| PCB 008 | PCB 066 | PCB 101 | PCB 151 | PCB 182 |
| PCB 018 | PCB 070 | PCB 105 | PCB 153 | PCB 183 |
| PCB 020 | PCB 073 | PCB 106 | PCB 156 | PCB 187 |
| PCB 021 | PCB 074 | PCB 110 | PCB 158 | PCB 190 |
| PCB 028 | PCB 076 | PCB 115 | PCB 160 | PCB 194 |
| PCB 031 | PCB 080 | PCB 116 | PCB 163 | PCB 195 |
| PCB 033 | PCB 086 | PCB 118 | PCB 164 | PCB 196 |
| PCB 043 | PCB 087 | PCB 127 | PCB 168 | PCB 201 |
| PCB 044 | PCB 089 | PCB 128 | PCB 169 | PCB 203 |
| PCB 049 | PCB 090 | PCB 132 | PCB 170 |  |
| PCB 052 | PCB 093 | PCB 138 | PCB 174 |  |
| PCB 056 | PCB 095 | PCB 139 | PCB 177 |  |
| PCB 060 | PCB 097 | PCB 141 | PCB 180 |  |

**Table F-10. PCB Congeners, Including Co-Elution (IUPAC No.)**

**with DB-1 Column for TMDL Development**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCB 005 | PCB 061 | PCB 110 | PCB 160 | PCB 196 |
| PCB 008 | PCB 066 | PCB 117 | PCB 161 | PCB 201 |
| PCB 018 | PCB 069 | PCB 118 | PCB 162 | PCB 203 |
| PCB 020 | PCB 070 | PCB 125 | PCB 163 |  |
| PCB 021 | PCB 074 | PCB 128 | PCB 164 |  |
| PCB 028 | PCB 076 | PCB 132 | PCB 170 |  |
| PCB 031 | PCB 087 | PCB 138 | PCB 174 |  |
| PCB 033 | PCB 090 | PCB 139 | PCB 177 |  |
| PCB 043 | PCB 095 | PCB 141 | PCB 180 |  |
| PCB 044 | PCB 097 | PCB 149 | PCB 182 |  |
| PCB 049 | PCB 099 | PCB 151 | PCB 183 |  |
| PCB 052 | PCB 101 | PCB 153 | PCB 187 |  |
| PCB 056 | PCB 105 | PCB 156 | PCB 194 |  |
| PCB 060 | PCB 106 | PCB 158 | PCB 195 |  |

D. Discharge Requirement Considerations

**1. Anti-backsliding.** This Order complies with the anti-backsliding provisions of CWA sections 402(o) and 303(d)(4) and 40 C.F.R. section 122.44(l), which generally require effluent limitations in a reissued permit to be as stringent as those in the previous permit. The requirements of this Order are at least as stringent as those in the previous order.

**2. Antidegradation.** This Order complies with the antidegradation provisions of 40 C.F.R. section 131.12 and State Water Board Resolution No. 68-16. It continues the status quo with respect to the level of discharge authorized in the previous order, which was adopted in accordance with antidegradation policies and thus serves as the baseline by which to measure whether degradation will occur. This Order does not allow for a reduced level of treatment or an increase in effluent limitations relative to those in the previous order.

**3. Stringency of Requirements for Mercury and PCBs.** This Order contains WQBELs for mercury and PCBs, which are no more stringent than required to implement CWA requirements. The mercury and PCBs WQBELs, which implement wasteload allocations, have been computed to satisfy the San Francisco Bay Mercury and PCBs TMDLs. Compliance with the WQBELs will allow the San Francisco Bay to come into attainment with mercury and PCBs water quality objectives necessary to protect beneficial uses.

V. Rationale for Receiving Water Limitations

No additional receiving water limits beyond those already specified in the Dischargers’ individual NPDES permits are necessary in this Order to satisfy the San Francisco Bay Mercury and PCBs TMDLs.

VI. Rationale for Provisions

A. Standard Provisions

Attachment D of each individual NPDES permit contains standard provisions that apply to all NPDES permits in accordance with 40 C.F.R. section 122.41 and additional conditions applicable to specific categories of permits in accordance with 40 C.F.R. section 122.42. Dischargers must comply with these provisions.

In accordance with 40 C.F.R. section 123.25(a)(12), states may omit or modify conditions to impose more stringent requirements. Attachment G of each individual NPDES permit contains contain sampling and reporting requirements for mercury and PCBs and additional standard provisions that supplement the federal standard provisions in Attachment D. This Order omits the federal conditions that address enforcement authority specified in 40 C.F.R. sections 122.41(j)(5) and (k)(2) because the State’s enforcement authority under the Water Code is more stringent. In lieu of these conditions, this Order incorporates Water Code section 13387(e) by reference.

B. Monitoring and Reporting

CWA section 308 and 40 C.F.R. sections 122.41(h), 122.41(j)-(l), 122.44(i), and 122.48 require that NPDES permits specify monitoring and reporting requirements. Water Code sections 13267 and 13383 also authorize the Regional Water Board to establish monitoring, inspection, entry, reporting, and recordkeeping requirements. The MRP establishes monitoring, reporting, and recordkeeping requirements that implement federal and State requirements. For more background regarding these requirements, see Fact Sheet section VII. Regional Water Board Order No. R2-2016-0008 allows the Discharger to opt for certain alternate monitoring requirements.

C. Special Provisions

1. Reopener Provisions

This reopener is to cover any changes or modifications to the mercury or PCBs TMDLs.

1. Triggers for Additional Mercury Control

Mass and concentration-based triggers were developed to allow for early required actions in the event an increasing trend in mercury discharge is observed by a Discharger. The purpose of the triggers is to evaluate the source of new mercury and identify a method for reduction before levels become elevated.

Consistent with the San Francisco Bay Mercury TMDL, mass triggers for Municipal and Industrial Dischargers are equivalent to the individual mass-based limitations stated in this Order, with the exception that compliance with the mass-based limitations are determined monthly, instead of annually, using a rolling 12-month average. This is necessary in order to capture any mercury load increases earlier to allow development and implementation of reduction measures that may avoid an actual effluent limit violation.

For concentration-based triggers, there are two broad categories of municipal facilities: (1) those that provide secondary treatment, and (2) those that provide advanced secondary treatment. Facilities providing advanced treatment have better performance, hence lower effluent concentrations than those providing secondary treatment. Therefore, the trigger concentrations for advanced facilities are lower than those for secondary treatment facilities.

Consistent with the TMDL implementation plan, the proposed effluent mercury concentration trigger values for municipal secondary treatment facilities are a daily maximum of 0.065 μg/l total mercury (derived from the 99th percentile concentration of effluent data collected from January 2000 to September 2002) and a monthly average of 0.041 μg/l total mercury (derived from the 95th percentile concentration of effluent data collected from January 2000 to September 2002). For facilities providing advanced treatment, the proposed concentration triggers are a daily maximum of 0.021 μg/l total mercury (the 99th percentile concentration) and a monthly average of 0.011 μg/l total mercury (the 95th percentile concentration).

Consistent with the TMDL implementation plan, the proposed effluent trigger concentrations for Industrial Dischargers are a daily maximum of 0.062 μg/l total mercury (derived from the 99th percentile concentration of petroleum-refinery effluent data collected from January 2000 to September 2002) and a monthly average of 0.037 μg/l total mercury (derived from the 95th percentile concentration of petroleum-refinery effluent data collected from January 2000 to September 2002).

Consistent with the TMDL, if a Discharger exceeds either its mass or concentration trigger, this Order requires the Discharger to report the exceedance in its Self-Monitoring Report and include the following:

**a.** Evaluation of the cause of the trigger exceedance

**b.** Evaluation of the effectiveness of existing pollution prevention or pretreatment programs and methods for preventing future exceedances;

**c.** Evaluation of the feasibility and effectiveness of technology enhancements to improve plant performance.

This Order provides for 130 days to provide this report, which allows for 30 days for standard laboratory turnaround on ultra clean samples, plus 40 days for accelerated monitoring to verify and better characterize trigger exceedances, and finally the 60-day timeframe from the TMDL implementation plan to submit the report. The Regional Water Board will pursue enforcement action against Dischargers that do not respond to exceedances of triggers or do not implement actions to correct and prevent trigger exceedances. Determination of appropriate actions will be based on an updated assessment of source control measures and wastewater treatment technologies applicable for the term of each issued or reissued permit.

The TMDL implementation plan requires the permit to specify that an exceedance of a trigger level would trigger a Discharger to take corrective actions. The TMDL implementation plan explains that one of the concepts behind requiring triggered actions is to ensure that wastewater dischargers continue ongoing operation, maintenance, and performance of their treatment facilities. This Order is consistent with the TMDL because it allows accelerated monitoring to determine if ongoing performance was maintained before corrective measures must be taken. Accelerated weekly monitoring for at least six events that would span over two months would provide reasonable and convincing weight of evidence that the first initial trigger was either an anomaly or a spurious source and could be disregarded. These additional samples would also help to characterize the duration and magnitude of the exceedance and help with development of the action plan should one be necessary.

See Appendix F-1 for an example of actions required in response to initial trigger exceedances.

1. Mercury and PCBs Source Control Program

The San Francisco Bay Mercury and PCBs TMDLs both require that Municipal and Industrial Dischargers develop and implement programs to identify and control manageable sources of mercury and PCBs. Therefore, this Order requires Dischargers to implement source control programs to reduce mercury and PCBs loads to their respective treatment plants.

1. Risk Reduction Programs

The San Francisco Bay Mercury and PCBs TMDLs require Municipal and Industrial Dischargers to develop and implement effective programs to reduce mercury‑related and PCBs-related risks to human health and aquatic organisms and wildlife, and to quantify risk reductions resulting from these activities. This Order requires Dischargers to implement these measures to reduce mercury and PCB-related risks.

In this effort, the Regional Water Board will work with the California Office of Environmental Health Hazard Assessment, the California Department of Public Health, and other organizations including Dischargers that pursue risk management as part of their mercury and PCB-related programs. For an effective and efficient regional program, this Order allows for third parties, such as the Regional Monitoring Program, to conduct these programs if Dischargers provide funding for this purpose.

1. Mercury and PCBs Discharge Adjustments for Recycled Wastewater Use by Industrial Dischargers

The Regional Water Board encourages water recycling pursuant to California Water Code sections 13510 through 13512. Recycled wastewater can preserve potable water supply sources. Consistent with Basin Plan section 4.6.1.1, the Mercury or PCBs Adjustment provided in this Order allows Municipal Dischargers, who produce recycled water, and Industrial Dischargers, who use recycled water in its industrial processes, to not get penalized.

The Adjustments are only applicable if the mercury or PCBs in the recycled wastewater is ultimately discharged through an Industrial Discharger’s outfall. The Adjustments are calculated based on mass balance principles and will not result in any net increase in mercury or PCBs loadings to San Francisco Bay.

The Mass Adjustment is subtracted from one Industrial Discharger and is then added to the Municipal Discharger who supplied the recycled wastewater who would have otherwise discharged that mercury or PCBs through its municipal treatment plant outfall. Local impacts from this shifting in load would be minimal because the municipal or industrial discharge would be discharged to the same receiving water body; the cost of water transport between facilities that are very far apart would make the reuse project infeasible.

A Concentration Adjustment is provided because a typical reuse project for an industrial facility involves using the recycled water in cooling towers or boilers where the concentration of mercury or PCBs increases through evaporative losses. The blowdown would eventually go to the Industrial Discharger’s sewer and potentially elevate its discharge concentration. Since the concentration limit is based on past performance, future recycled wastewater use could impact the Industrial Discharger’s compliance with the performance limitation. Unlike the Mass Adjustment, it is inappropriate to add the Concentration Adjustment to the supplying Municipal Discharger because an increase in concentration that occurs at the industrial facility does not affect the Municipal Discharger’s performance.

1. PCBs Discharge Adjustment for Urban Stormwater Treatment by Municipal Dischargers

The Regional Water Board recognizes that routing urban runoff through municipal wastewater treatment facilities may be an efficient means of reducing PCBs and other particle-associated contaminant loads to the San Francisco Bay. For this reason, the San Francisco Bay PCBs TMDL includes a reserve allocation of 1.0 kg/year for municipal wastewater treatment plants to treat urban runoff (specified in Basin Plan Table 7.2.3-2). This provision provides a mechanism for Municipal Dischargers to receive a credit for treating urban runoff that would otherwise be discharged directly to San Francisco Bay.

As with the Adjustments for Industrial Dischargers, Adjustments are calculated based on mass balance principles and will not result in any net increase in PCBs loadings to San Francisco Bay. Unlike the use of recycled water, urban runoff diversions will occur in intermittent periods of time, most likely over a period of hours. For this reason, it is not possible to coordinate sampling of influent and effluent with the precision applied for recycled water credits. Additionally, the concentrations of PCBs in urban runoff are expected to be much more variable than those found in recycled water. East Bay Municipal Utility District’s study, *Characterization of Stormwater Flows, Diversion of Dry Weather and First Flush Flows to a Publicly-Owned Treatment Works* (July 2010) found the concentrations of PCBs in dry weather runoff to be almost an order of magnitude lower than those found in wet weather. As such, when determining credits for urban runoff diversions, this Order groups them into two categories: (1) dry weather diversions and (2) wet weather diversions.

During this Order term, the Municipal Discharger may use the entire influent PCBs mass for the concentration adjustment described in Provision VI.C.6.

VII. Rationale for Monitoring and Reporting Program (MRP)

Attachment E contains the MRP for this Order. It specifies sampling stations, mercury and PCBs monitoring frequencies, and reporting requirements. The following provides the rationale for these requirements.

Basin Plan sections 7.2.2.6 and 7.2.3.6 require Dischargers to monitor and report mercury and PCBs discharge loads. Effluent monitoring is also necessary to capture any increases in loading and develop and implement reduction measures in advance of an effluent limitation exceedance.

This Order retains the monitoring frequencies from the previous order. The monitoring frequencies specified in the MRP are dependent on each Discharger’s contribution of mercury and PCBs, and its resources to conduct the monitoring. Those with larger flows are required to monitor more frequently.

Compliance with effluent limitations must be determined using an approved method under 40 C.F.R. Part 136. For PCBs, this is U.S. EPA Method 608. Consistent with the San Francisco Bay PCBs TMDL, this Order also requires each Discharger to monitor and report PCBs congeners using the proposed U.S. EPA Method 1668C, which is capable of quantifying PCBs that are present at lower levels than U.S. EPA Method 608 used to monitor PCBs Aroclors. The Regional Water Board will use U.S. EPA Method 1668C data to verify assumptions and evaluate the need to further refine wasteload allocations in the TMDL.

VIII. Public Participation

The Regional Water Board considered the issuance of WDRs that will serve as an NPDES permit for point source discharges of mercury and PCBs from Municipal and Industrial Dischargers. As a step in the WDR adoption process, Regional Water Board staff developed tentative WDRs and encouraged public participation in the WDR adoption process.

**A. Notification of Interested Parties.** The Regional Water Board notified the Dischargers and interested agencies and persons of its intent to prescribe WDRs for the discharges and provided an opportunity to submit written comments and recommendations. Notification was provided through the Oakland Tribune. The public had access to the agenda and any changes in dates and locations through the Regional Water Board’s website at [http://www.waterboards.ca.gov/sanfranciscobay](mailto:NPDES_Wastewater@waterboards.ca.gov).

**B. Written Comments.** Interested persons were invited to submit written comments concerning the tentative WDRs as explained through the notification process. Comments were to be submitted either in person or by mail to the Executive Officer at the Regional Water Board at 1515 Clay Street, Suite 1400, Oakland, California 94612, to the attention of James Parrish.

For full staff response and Regional Water Board consideration, the written comments were due at the Regional Water Board office by 5:00 p.m on **September 8, 2017.**

**C. Public Hearing.** The Regional Water Board held a public hearing on the tentative WDRs during its regular meeting at the following date and time, and at the following location:

Date: **November 8, 2017**

Time: 9:00 am

Location: Elihu Harris State Office Building

1515 Clay Street, 1st Floor Auditorium

Oakland, CA 94612

Contact: James Parrish, (510) 622-2381, James.Parrish@waterboards.ca.gov.

Interested persons were invited to attend. At the public hearing, the Regional Water Board heard testimony pertinent to the discharge, WDRs, and permit. For accuracy of the record, important testimony was requested to be in writing.

Dates and venues change. The Regional Water Board web address is [http://www.waterboards.ca.gov/sanfranciscobay](mailto:NPDES_Wastewater@waterboards.ca.gov), where one could access the current agenda for changes in dates and locations.

**D. Reconsideration of Waste Discharge Requirements.** Any aggrieved person may petition the State Water Board to review the Regional Water Board decision regarding the final WDRs. The State Water Board must receive the petition at the following address within 30 calendar days of the Regional Water Board action:

State Water Resources Control Board

Office of Chief Counsel

P.O. Box 100, 1001 I Street

Sacramento, CA 95812-0100

For instructions on how to file a petition for review, see http://www.waterboards.ca.gov/public\_notices/petitions/water\_quality/wqpetition\_instr.shtml.

**E. Information and Copying.** The San Francisco Bay Mercury and PCBs TMDLs, tentative order, related supporting documents, and comments received are on file and may be inspected at the address above at any time between 9:00 a.m. and 5:00 p.m., Monday through Friday. Copying of documents may be arranged by calling (510) 622-2300.

**F. Register of Interested Persons.** Any person interested in being placed on the mailing list for information regarding the WDRs and NPDES permit should contact the Regional Water Board, reference the Facility, and provide a name, address, and phone number.

**G. Additional Information.** Requests for additional information or questions regarding this Order should be directed to James Parrish, at (510) 622-2381, or James.Parrish@waterboards.ca.gov.

**APPENDIX F-1**

**WHEN REQUIRED ACTIONS ARE TRIGGERED**

Discharger X is subject to the following triggers:

Average Monthly Trigger = 0.041 μg/L

Maximum Daily Trigger = 0.065 μg/L

12-month Mass Emission Trigger = 0.91 kg/yr

A sample was collected on May 4th is 0.046 μg/L, with the results received on May 30th by Discharger X from its contract laboratory.

**Discharger Action 1:** Initiate accelerated monitoring (weekly or more frequent) as soon as practical (within 48 hours) after receipt of sample result above trigger level (0.046 μg/L is above the monthly trigger of 0.041 μg/L).

**Discharger Action 2:** Report this exceedance in its cover sheet for the May self-monitoring report (due June 30th), and continue to report mercury data on the cover sheet until successful completion.

**Discharger Action 3:** Continue accelerated monitoring until not less than a total of 6 new samples have been collected.

Discharger X’s accelerated samples reveal the following results:

|  |  |  |
| --- | --- | --- |
| **Sample Date** | **Sample Result, μg/L** | **12-month mass, kg/yr** |
| (May 4) | **(0.046)** | 0.80 |
| June 1 | 0.031 | 0.79 |
| June 5 | 0.059 | 0.82 |
| June 14 | 0.023 | 0.81 |
| June 18 | 0.055 | 0.82 |
| June 30 | 0.040 | 0.82 |
| July 5 | 0.029 | 0.81 |

**Discharger Action 4:** Initiate, no later than July 5, development of Action Plan for Mercury Reduction.

**Note**: Despite the fact that the one sample for July is below all three triggers, the average of the samples in June is above the monthly average trigger.

**Discharger Action 5:** Discharger X may shift to monthly monitoring after collection of the 6th accelerated sample.

Additional monitoring results:

|  |  |  |
| --- | --- | --- |
| **Sample Date** | **Sample Result, μg/L** | **12-month mass, kg/yr** |
| August 11 | 0.027 | 0.80 |
| September 14 | 0.042 | 0.78 |
| October 5 | 0.042 | 0.075 |
| October 7 | ND (<0.0005) |
| November 5 | 0.035 | 0.81 |
| December 10 | 0.022 | **0.93** |
| January 5 | 0.018 | **0.94** |
| February 14 | 0.028 | 0.85 |
| March 25 | 0.010 | 0.81 |
| April 7 | 0.023 | 0.75 |

**Discharger Action 6:** Submit and implement Action Plan for Mercury Reduction (due 130 days after May 30).

**Note:** Despite the July and August samples being below both concentration triggers, three consecutive months below **all** triggers are necessary before the Action Plan activities are no longer required. The May sample is still above the monthly trigger.

**Note:** In September, though that sample is above the monthly concentration trigger, accelerated monitoring is not required again because Discharger X has already been triggered into Action Plan mode.

**Note:** In December, though the concentrations have been below concentration triggers for three consecutive months, Discharger X must continue with the Action Plan because its 12-month running average mass discharge still exceeds the mass trigger.

**Discharger Action 7: R**eport on current mercury reduction efforts in its Annual Self-Monitoring Report due February 1st.

In April, three consecutive months show successful completion of this effort. Discharger X is no longer required to further implement its Action Plan, and may thus return to routine monitoring. Discharger X reports its mercury reduction efforts in its Annual Self-Monitoring Report due the following February.

**APPENDIX F-2**

**CALCULATION OF CONCENTRATION-BASED MERCURY LIMITS**

**Introduction**

To calculate concentration-based mercury limitations that are consistent with the assumptions and requirements of the San Francisco Bay Mercury TMDL, the Regional Water Board analyzed mercury data from 2000 to 2003 and grouped that data into three categories (municipal secondary treatment, municipal advanced secondary treatment involving filtration, and industrial treatment). The statistical analysis used data from 17 secondary treatment plants, 7 advanced secondary treatment plants, and 5 petroleum refineries.

The purpose of pooling mercury data to calculate limitations based on category of treatment and/or processes that are similar was to reduce the likelihood of penalizing Dischargers who have implemented effective control measures and are already performing well, and rewarding other Dischargers who may not have implemented similar measures.

**Data Analysis of Municipal Treatment Facilities**

Regional Water Board staff analyzed mercury data from all treatment plants that were using the Regional Water Board’s electronic reporting system. Mercury data that did not appear to result from ultra‑clean sampling because of high detection limits were removed (i.e., EBMUD data from January 2000 through May 2001, and the San Francisco City and County Southeast Plant from October 21, 2003). Additionally, when detection limits were very low (e.g., the practical quantification limit [PQL] equaled 0.5 ng/L and the method detection limit equaled 0.24 ng/L), Regional Water Board staff censored data at the PQL. Finally, the Regional Water Board did not use data from Silicon Valley Clean Water because its treatment plant did not always filter treated wastewater, which made it difficult to categorize the plant as performing secondary or advanced secondary treatment.

**Secondary Treatment Plants**

The Regional Water Board’s analysis of secondary treatment plants indicates that mercury data fit a log‑normal distribution since the data closely follow the line of normality, as shown in Figure 1 below:

**Figure 1. Probability Plot of Mercury Data for Secondary Treatment Plants**



Because natural log-transformed mercury data for secondary treatment plants fit a normal distribution, it was possible to calculate performance-based limits based on select percentiles. For secondary treatment plants (data sample size of 984), the mean and standard deviation in the natural log phase were -4.5212 and 0.7188, respectively. Regional Water Board staff calculated daily, weekly, and monthly mercury limits based on the 99.87th percentile (3 standard deviations above the mean), the 99.57th percentile (2.625 standard deviations above the mean), and the 99.38th percentile (2.5 standard deviations above the mean).

**Table 1. Mercury Limits for Secondary Treatment Plants**

|  |  |  |
| --- | --- | --- |
| **Percentile** | **Averaging Period** | **Mercury Limit (ng/L)** |
| 99.87th | Daily | 94 |
| 99.57th | Weekly | 72 |
| 99.38th | Monthly | 66 |

**Advanced Secondary Treatment Plants**

The Regional Water Board’s analysis of advanced secondary treatment plants indicates those data also fit a log-normal distribution since the data follow the line of normality, as shown in Figure 2 below:

**Figure 2. Probability Plot of Mercury Data for Advanced Secondary Treatment Plants**



Because natural log-transformed mercury data for advanced secondary treatment plants fit a normal distribution, it was possible to calculate performance-based limits based on select percentiles. For advanced secondary treatment plants (data sample size of 434), the mean and standard deviation in the natural log phase were -5.3457 and 0.6664, respectively. Regional Water Board staff calculated daily, weekly, and monthly mercury limits based on the 99.87th percentile, the 99.57th percentile, and the 99.38th percentile.

**Table 2. Mercury Limits for Advanced Secondary Treatment Plants**

|  |  |  |
| --- | --- | --- |
| **Percentile** | **Averaging Period** | **Mercury Limit (ng/L)** |
| 99.87th | Daily | 35 |
| 99.57th | Weekly | 27 |
| 99.38th | Monthly | 25 |

**Data Analysis of Industrial Treatment Facilities**

The Regional Water Board analyzed mercury data from five petroleum refineries that report data to the Water Board’s electronic reporting system. Regional Water Board staff determined that a number of data points from three of the refineries (i.e., Chevron, ConocoPhillips, and Shell) were not indicative of treatment plant performance, and therefore, were removed. Additionally, when detection limits were very low, the Regional Water Board censored data at the PQL.

The Regional Water Board’s analysis of five Bay Area refineries indicated that mercury data fit a log‑normal distribution since the data closely follow the line of normality, as shown in Figure 3 below:

**Figure 3. Probability Plot of Mercury Data for Bay Area Refineries**



Because natural log-transformed mercury data fit a normal distribution, it was possible to calculate performance-based limits based on select percentiles. For refineries (data sample size of 296), the mean and standard deviation in the natural log phase were -4.7000 and 0.8654, respectively. Regional Water Board staff calculated daily, weekly, and monthly mercury limits based on the 99.87th percentile (3 standard deviations above the mean), the 99.57th percentile (2.625 standard deviations above the mean), and the 99.38th percentile (2.5 standard deviations above the mean).

**Table 3. Mercury Limits for Industries Using Petroleum Refinery Performance**

|  |  |  |
| --- | --- | --- |
| **Percentile** | **Averaging Period** | **Mercury Limit (ng/L)** |
| 99.87th | Daily | 122 |
| 99.57th | Weekly | 88 |
| 99.38th | Monthly | 79 |

**APPENDIX F-3**

**SUMMARY OF PCBs LOADS**

**Table 1. PCBs Loads from Municipal Dischargers (Secondary Treatment)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Discharger** | **PCBs Loads (kg/yr) Normalized** | | | |
| **Year** | | | |
| **2013** | **2014** | **2015** | **2016** |
| Benicia | 0.001027366 | 0.000702512 | 0.001330807 | 0.001729332 |
| Benicia | 0.000361876 | 0.001375673 | 0.000691841 | 0.000834243 |
| Burlingame | 0.00130887 | 0.000888176 | 0.000736908 | 0 |
| Burlingame | 0.001422589 | 0.0010376 | 0.000834373 | 0.000655316 |
| Burlingame | 0.001675026 | 0.000914767 | 0.001560205 | 0.000426249 |
| Burlingame | 0.000504476 | 0.001043412 | 0.001156979 | 0.000476454 |
| Calistoga | 0 | 6.29016E-05 | 5.50621E-05 | 7.66743E-05 |
| CCCSD | 0.025095234 | 0.006116432 | 0.013747729 | 0.008623899 |
| CCCSD | 0.003264302 | 0.005624446 | 0.018697144 | 0.011315563 |
| CCCSD | 0.007228911 | 0.017594892 | 0.00797204 | 0.009579598 |
| CCCSD | 0.005032644 | 0.011936161 | 0.011321103 | 0.010361204 |
| CCCSD | - | 0.012157971 | - | - |
| Central Marin | 0.000756037 | 0.004998032 | 0.003114993 | 0.003365655 |
| Central Marin | 0.000943599 | 0.001978248 | 0.002112238 | 0.002093666 |
| Central Marin | 0.001152937 | 0.002498263 | 0.003452139 | 0.001961261 |
| Central Marin | 0.001224986 | 0.002963676 | 0.002842755 | 0.00240807 |
| Delta Diablo | 0.000942957 | 0.002947538 | 0.002737323 | 0.002280301 |
| Delta Diablo | 0.000779033 | 0.002095981 | 0.002335431 | 0.002723372 |
| Delta Diablo | 0.0006008 | 0.001712705 | 0.003653966 | 0.001881737 |
| Delta Diablo | 0.00079602 | 0.002938497 | 0.002095972 | 0.003134687 |
| EBDA | 0.014436013 | 0.02736045 | 0.029149428 | 0.038618654 |
| EBDA | 0.006465304 | 0.029425402 | 0.047366545 | 0.02194252 |
| EBDA | 0.011573873 | 0.041672703 | 0.023974444 | 0.031044006 |
| EBDA | 0.021440442 | 0.074240246 | 0.038079977 | 0.038907642 |
| EBMUD | 0.021144144 | 0.039301374 | 0.040613268 | 0.034658698 |
| EBMUD | 0.015332442 | 0.052093417 | 0.038458924 | 0.016606272 |
| EBMUD | 0.024145186 | 0.024682848 | 0.027393817 | 0.030472948 |
| EBMUD | 0.029025869 | 0.065442361 | 0.04044419 | 0.031946445 |
| Las Gallinas | 0.003546046 | 0.003804885 | 0.003110253 | 0.004953674 |
| Las Gallinas | - | 0.003239256 | 0.001178193 | 0.002048252 |
| Millbrae | 0.001520444 | 0.002647206 | 0.00154215 | 0.001174746 |
| Millbrae | 0.00209798 | 0.000939631 | 0.000980862 | 0.000539392 |
| Napa | 0.000679109 | 0.001060108 | 0.001661206 | 0.000525912 |
| Napa | 0 | 0.003697313 | 0.001400147 | 4.04505E-05 |
| Napa | 0.000542489 | 0.00187091 | 0.001107936 | 0.00040638 |
| Novato | 0.00033085 | 0.003548261 | 0.003399076 | 0.003348265 |
| Novato | 0.000477889 | 0.001653349 | 0.00248184 | 0.00104419 |
| Novato | 0.000523464 | 0.000922565 | 0.001123615 | 0.002141501 |
| Petaluma | 1.95813E-05 | 0.001564884 | 0.000206902 | 0.000166016 |
| Petaluma | 1.63824E-05 | 0.00040099 | 4.94945E-05 | 1.01493E-05 |
| Petaluma | 4.56325E-05 | 0.000418103 | 2.92188E-05 | 4.48137E-05 |
| Pinole | 0.001856034 | 0.001040543 | 0.000598382 | 0.000595688 |
| Pinole | 0.000724087 | 0.000899116 | 0.000587417 | 0.00097685 |
| Rodeo | 0.000162977 | 0.000152026 | 0.000161064 | 0.001340938 |
| Rodeo | 0.00015571 | 0.000946098 | - | - |
| San Mateo | 0.002015566 | 0.003454585 | 0.006283256 | 0.003094478 |
| San Mateo | 0.001610267 | 0.005098295 | 0.007244187 | 0.005104726 |
| San Mateo | 0.004401604 | 0.008940223 | 0.005703687 | 0.005456581 |
| San Mateo | 0.001533621 | 0.005745627 | 0.005194759 | 0.005324376 |
| SASM | 0.004598506 | 0.004239067 | 0.003155624 | 0.003602825 |
| SASM | 0.002120129 | 0.003810661 | 0.001941614 | 0.003425009 |
| Sausalito-Marin | 0.001869741 | 0.003155468 | 0.001941475 | - |
| Sausalito-Marin | 0.002131512 | 0.002195343 | 0.001243779 | 0.003605147 |
| SD #5 - Paradise Cove | 1.68706E-05 | 4.83457E-05 | 3.11404E-05 | 0.000309092 |
| SD #5 - Tiburon | 0.000216382 | 0.000632623 | 0.000697987 | 0.002652883 |
| SD #5 - Tiburon | 0.00020725 | 0.000529257 | - | - |
| SF Southeast | 0.014440261 | 0.016051745 | 0.026723587 | 0.017280144 |
| SF Southeast | 0.013196184 | 0.027851261 | 0.020763159 | 0.04175091 |
| SF Southeast | 0.016433838 | 0.035862344 | 0.014595356 | 0.041059742 |
| SF Southeast | 0.016014992 | 0.052611259 | 0.061609612 | 0.030861908 |
| SFO Airport | 0.000254427 | 0.001230514 | 0.000572453 | 0.000675278 |
| SFO Airport | 0.000249322 | 0.001034041 | 0.000581651 | 0.00125239 |
| Silicon Valley Clean Water | 0.007886899 | 0.00182581 | 0.004316189 | 0.026428526 |
| Silicon Valley Clean Water | 0.002780926 | 0.003606276 | 0.002235643 | 0.002665677 |
| Silicon Valley Clean Water | 0.002660565 | 0.002797678 | 0.004337324 | 0.01346841 |
| Silicon Valley Clean Water | 0.002518986 | 0.008893033 | 0.004323485 | 0.013385183 |
| Sonoma Valley County SD | 0.000240769 | 5.29543E-05 | 4.24765E-05 | 2.20148E-06 |
| Sonoma Valley County SD | 6.61511E-05 | 0.000221437 | 7.29421E-05 | 0.000580791 |
| South SF and San Bruno | 0.003048769 | 0.002131267 | 0.001674849 | 0.001597152 |
| South SF and San Bruno | 0.001769671 | 0.002469812 | 0.001199606 | 0.000926471 |
| South SF and San Bruno | 0.00496287 | 0.001494728 | 0.001109731 | 0.002337297 |
| South SF and San Bruno | 0.005457058 | 0.002179173 | 0.001329856 | 0.001733714 |
| Treasure Island | 0.001747733 | 0.004870548 | 0.004315642 | 0.002300291 |
| Treasure Island | 0.004249545 | 0.00406025 | 0.002893406 | 0.006282947 |
| Vallejo | 0.001716043 | 0.005148906 | 0.008790509 | 0.02676705 |
| Vallejo | 0.002755984 | 0.00640477 | 0.006212837 | 0.00639365 |
| Vallejo | 0.00192151 | 0.00722804 | 0.007025443 | 0.005516793 |
| Vallejo | 0.004372058 | 0.006308582 | 0.006572656 | 0.00664987 |
| West County Agency | 0.002229805 | 0.019487494 | 0.004256061 | 0.002960736 |
| West County Agency | 0.002478752 | 0.003803865 | 0.000569599 | 0.003804654 |
| West County Agency | 0.003510146 | 0.001874279 | 0.003403962 | 0.003694124 |
| West County Agency | 0.002888309 | 0.003053117 | 0.002981216 | 0.018929139 |
| Yountville | 0.000428631 | 6.02942E-05 | 3.42156E-05 | 6.00723E-05 |
| **Total** | **0.351381261** | **0.7250749** | **0.61152833** | **0.639421925** |

**Table 2. PCBs Loads from Municipal Dischargers (Advanced Secondary Treatment)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Discharger** | **PCBs Loads (kg/yr) Normalized** | | | |
| **Year** | | | |
| **2013** | **2014** | **2015** | **2016** |
| American Canyon | 1.2443E-05 | 2.19831E-05 | 3.10612E-05 | 2.12206E-05 |
| American Canyon | 3.85216E-05 | 2.98458E-05 | 2.23113E-05 | 5.76749E-06 |
| Fairfield | 6.40732E-05 | 0.000124309 | 0.004808032 | 0.003827038 |
| Fairfield | 0.002464056 | 0.003985308 | 2.23113E-05 | 0.000525541 |
| Fairfield | 0.000444199 | 0.002023944 | 0.004808032 | 0.003827038 |
| Fairfield | 0.002387212 | 0.00244248 | 0.003454068 | 0.000525541 |
| Mt. View | 0.000380578 | 0.000431779 | 0.000251154 | 0.000444951 |
| Mt. View | 0.00051271 | 0.000644994 | 0.00039511 | 0.000551976 |
| Palo Alto | 0.001500471 | 0.011737367 | 0.003781006 | 0.010828444 |
| Palo Alto | 0.002212234 | 0.004885093 | 0.008983983 | 0.005599664 |
| Palo Alto | 0.00121759 | 0.004168968 | 0.008707744 | 0.007144422 |
| Palo Alto | 0.001908616 | 0.009915734 | 0.007325264 | 0.006102645 |
| San Jose | 0.012930405 | 0.006865736 | 0.007628329 | 0.006405388 |
| San Jose | 0.005241254 | 0.011837227 | 0.006466247 | 0.006778259 |
| San Jose | 0.005114915 | 0.005955494 | 0.004720837 | 0.006053584 |
| San Jose | 0.004747444 | 0.010491396 | 0.005558841 | 0.006191107 |
| Sunnyvale | 0.010757959 | 0.006953892 | 0.019647826 | 0.007845579 |
| Sunnyvale | 0.001445272 | 0.00192814 | 0.001944189 | 0.001934008 |
| Sunnyvale | 0.003550054 | 0.005343286 | 0.002960746 | 0.000362331 |
| Sunnyvale | 0.005139162 | 0.002722424 | 0.005309606 | 0.003968065 |
| **Total** | **0.062069169** | **0.092509399** | **0.096826697** | **0.078942567** |

**Table 3. PCBs Loads from Petroleum Refineries**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Discharger** | **PCBs Loads (kg/yr) Normalized** | | | |
| **Year** | | | |
| **2013** | **2014** | **2015** | **2016** |
| Chevron | 0.002441221 | 0.001204925 | 0.001048217 | 0.001415608 |
| Chevron | 0.004242096 | 0.002501528 | 0.00092711 | 0.000675529 |
| Chevron | 0.002122772 | 0.001217467 | 0.000393442 | 0.000427429 |
| Chevron | 0.001157919 | 0.000595771 | 0.000592657 | 0.000451338 |
| Phillips 66 | 4.76663E-06 | 0.000821772 | 0.00206903 | 0.002063512 |
| Phillips 67 | 0 | 0.000672565 | 0.002020933 | 3.21561E-05 |
| Phillips 68 | 1.55848E-05 | 0 | 0.001062993 | 0 |
| Phillips 69 | 2.52666E-05 | 0 | 0.000810313 | 0 |
| Shell | 0.000286148 | 0.000209112 | 6.67773E-05 | 0.001512766 |
| Shell | 0.000162484 | 0.000229259 | 3.5482E-05 | 8.988E-05 |
| Shell | 5.1977E-05 | 0.00035582 | 7.10011E-05 | 4.81461E-05 |
| Shell | 3.11282E-05 | 6.84687E-05 | 9.6932E-05 | 0 |
| Shell | - | - | 2.50889E-05 | - |
| Tesoro | 0 | 0.000108397 | 6.02659E-05 | 6.545E-06 |
| Tesoro | 0.000102595 | 0.000106865 | 3.02851E-05 | 1.26933E-05 |
| Tesoro | 5.16372E-05 | 9.58012E-05 | 4.37745E-05 | 5.17775E-05 |
| Tesoro | 0.000141868 | 9.19044E-06 | 4.31566E-05 | 4.19221E-05 |
| Valero | 0 | 1.0391E-05 | 1.38142E-05 | 0 |
| Valero | 0 | - | 0.000250494 | 3.46442E-05 |
| Valero | - | - | 5.9889E-06 | 0 |
| **Total** | **0.010837463** | **0.008207332** | **0.009667756** | **0.006863947** |

**Table 4. PCBs Loads from Non-Petroleum Refineries**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Discharger** | **PCBs Loads (kg/yr) Normalized** | | | |
| **Year** | | | |
| **2013** | **2014** | **2015** | **2016** |
| C&H Sugar | 0.001244311 | 0.00059048 | 0.0001625 | 0.005711281 |
| C&H Sugar | - | 6.17967E-05 | 0.000140038 | 0.009294554 |
| Crockett Cogen | 0.000337716 | 0.000158455 | 0.000233529 | 4.46202E-06 |
| Eco Services | 1.53568E-05 | 2.77183E-05 | 3.32238E-05 | 4.1714E-05 |
| Eco Services | 1.10109E-05 | 8.55755E-06 | 3.61856E-05 | 4.92778E-05 |
| USS Posco | 0.000486777 | 0.000889019 | 0.001916503 | 0.002750828 |
| USS Posco | 0.001056105 | 0.000418653 | 0.000350865 | 0.000705606 |
| USS Posco | 0.000828925 | 0.00092713 | 0.000427598 | 0.000135538 |
| USS Posco | 0.000438991 | 0.000163214 | 0.001278389 | 0.00079062 |
| **Total** | **0.004419192** | **0.003245024** | **0.004578832** | **0.019483881** |

**APPENDIX F-4**

**DATA SUPPORTING PERFORMANCE-BASED PCBs LIMITATIONS**

|  |  |  |  |
| --- | --- | --- | --- |
| **Discharge Category – PCBs Data (µg/L)** | | | |
| Advanced Secondary | Secondary | Petroleum Refinery | Non-Petroleum Refinery |
| 0.000250 | 0.0079 | 0.000650 | 0.000860 |
| 0.000310 | 0.0011 | 0.000570 | 0.003700 |
| 0.000190 | 0.0047 | 0.000170 | 0.005600 |
| 0.000200 | 0.0022 | 0.000380 | 0.004300 |
| 0.000310 | 0.0057 | 0.000280 | 0.003400 |
| 0.000170 | 0.0014 | 0.000150 | 0.003400 |
| 0.000190 | 0.0037 | 0.000110 |  |
| 0.000130 | 0.0027 | 0.000150 |  |
| 0.000320 | 0.0026 | 0.000170 |  |
| 0.000170 |  | 0.000085 |  |
| 0.000120 |  |  |  |
| 0.000240 |  |  |  |
| 0.000190 |  |  |  |
| 0.000160 |  |  |  |